## General
General Data
Slack | 67 | Node slack
Vnom (kV) | 12.47
InternationalSystem | 0 | 1 = International units, 0 = English Units
DeltaLF | 0 | 1 = All loadas are in Delta and the Load Flow is in Delta
V_slack_ph_A | 0.989
V_slack_ph_B | 0.993
V_slack_ph_C | 0.99
Ang_slack_ph_A | -33.49
Ang_slack_ph_B | -153.64
Ang_slack_ph_C | 86.14

## Topology
Node A | Node B | Length (ft.) | Config. | SectionID
1 | 119 | 227 | 1 | SHE215_X7441ABC_91466 | OH
2 | 21 | 126 | 2 | SHE215_Y1380BAC_323434 | OH
3 | 217 | 363 | 3 | SHE215_PB0753A_91129 | UG
4 | 44 | 77 | 100 | SHE215_Y1005ABC_91523 | UG
4 | 222 | 199 | 4 | SHE215_Y1122C_634017 | OH
4 | 174 | 200 | 163 | SHE215_X4579BCA_323034 | OH
5 | 11 | 195 | 5 | SHE215_Y1255C_168971 | OH
5 | 268 | 201 | 161 | SHE215_X7266ABC_91525 | UG
6 | 95 | 145 | 6 | SHE215_Y1037BAC_553311 | OH
7 | 223 | 46 | 7 | SHE215_X7069CAB_479155 | OH
7 | 28 | 128 | 51 | SHE215_Y1121C_401446 | OH
8 | 224 | 153 | 8 | SHE215_Y1250CAB_323479 | OH
9 | 23 | 212 | 9 | SHE215_X7470C_401497 | UG
10 | 31 | 72 | 10 | SHE215_X4417BCA_401039 | OH
10 | 84 | 196 | 213 | SHE215_Y1007ABC_556707 | OH
11 | 240 | 163 | 64 | SHE215_Y1305BAC_165626 | OH
11 | 131 | 196 | 11 | SHE215_X7240BAC_479153 | OH
12 | 41 | 300 | 12 | SHE215_Y1346BAC_634004 | OH
13 | 101 | 112 | 92 | SHE215_X7005BAC_556705 | OH
13 | 219 | 173 | 13 | SHE215_X7070AC_168993 | OH
14 | 225 | 198 | 14 | SHE215_Y1281ABC_634068 | UG
15 | 144 | 85 | 260 | SHE215_X4351BAC_556355 | OH
15 | 215 | 191 | 246 | SHE215_Y1304BAC_165621 | OH
15 | 115 | 194 | 15 | SHE215_PB1880ABC_5116908 | UG
16 | 23 | 78 | 42 | SHE215_Y1229BAC_634013 | OH
16 | 138 | 137 | 16 | SHE215_X7109BAC_323440 | OH
17 | 121 | 202 | 17 | SHE215_X7487BAC_245895 | OH
18 | 98 | 255 | 18 | SHE215_X7189C_401438 | OH
19 | 69 | 99 | 19 | SHE215_X7190C_168969 | OH
20 | 128 | 114 | 20 | SHE215_X7P012B_245900 | UG
20 | 236 | 120 | 47 | SHE215_X7242CAB_479199 | OH
20 | 70 | 301 | 258 | SHE215_Y1325BAC_401439 | OH
21 | 226 | 267 | 21 | SHE215_Y1539BAC_320893 | OH
22 | 60 | 139 | 22 | SHE215_X7004BAC_246240 | OH
22 | 127 | 155 | 297 | SHE215_Y1420BAC_479173 | OH
22 | 48 | 271 | 77 | SHE215_Y1409BAC_246263 | OH
23 | 170 | 111 | 75 | SHE215_Y1253BAC_479163 | OH
23 | 227 | 115 | 23 | SHE215_Y1348CAB_91464 | OH
24 | 83 | 647 | 24 | SHE215_Y1031ABC_479204 | OH
25 | 228 | 73 | 25 | SHE215_Y1408CAB_320000 | OH
26 | 260 | 133 | 242 | SHE215_Y1258CAB_479207 | OH
26 | 229 | 256 | 26 | SHE215_Y1305CAB_475764 | OH
27 | 230 | 148 | 27 | SHE215_Y1227ABC_401495 | UG
27 | 3 | 236 | 181 | SHE215_X7P024ABC_5091900 | UG
27 | 153 | 304 | 186 | SHE215_Y1210A_323455 | OH
28 | 29 | 115 | 28 | SHE215_X4601BCA_633631 | OH
29 | 231 | 31 | 29 | SHE215_X7070A_91488 | OH
30 | 165 | 392 | 30 | SHE215_X7222BAC_556708 | OH
31 | 102 | 198 | 31 | SHE215_Y1314BAC_397859 | OH
32 | 18 | 150 | 32 | SHE215_X1P9128B_5139439 | UG
33 | 203 | 166 | 33 | SHE215_Y1255C_401479 | OH
34 | 19 | 203 | 34 | SHE215_Y1002C_91510 | OH
35 | 100 | 130 | 35 | SHE215_Y1219BAC_168994 | OH
36 | 206 | 120 | 36 | SHE215_Y1224A_4308571 | OH
37 | 193 | 83 | 191 | SHE215_Y1123C_168992 | OH
37 | 232 | 248 | 37 | SHE215_Y1324CB_397857 | OH
38 | 216 | 312 | 38 | SHE215_X7087A_634057 | OH
39 | 132 | 126 | 222 | SHE215_X4600BCA_556341 | OH
39 | 233 | 216 | 39 | SHE215_X7003BAC_246243 | OH
40 | 36 | 259 | 40 | SHE215_X4565BCA_91096 | OH
41 | 104 | 142 | 41 | SHE215_Y1335CAB_91463 | OH
42 | 194 | 190 | 211 | SHE215_Y1536CAB_88935 | OH
42 | 234 | 257 | 43 | SHE215_X7119BAC_168629 | OH
42 | 254 | 307 | 113 | SHE215_Y1121C_479203 | OH
43 | 235 | 84 | 44 | SHE215_X7068BAC_168977 | OH
43 | 283 | 93 | 219 | SHE215_Y1036BAC_88062 | OH
44 | 188 | 244 | 45 | SHE215_PB1881A_5090162 | UG
45 | 270 | 136 | 293 | SHE215_PB1840CAB_5066755 | UG
45 | 55 | 203 | 46 | SHE215_X7068BAC_91487 | OH
45 | 185 | 270 | 189 | SHE215_X7093A_246272 | OH
46 | 126 | 138 | 48 | SHE215_X7419AB_91113 | OH
47 | 204 | 221 | 49 | SHE215_X4082CAB_401057 | OH
48 | 237 | 40 | 50 | SHE215_Y1608ACB_5095973 | UG
49 | 76 | 77 | 52 | SHE215_X7269BAC_246242 | OH
49 | 243 | 185 | 79 | SHE215_Y1304BAC_630617 | OH
50 | 32 | 57 | 53 | SHE215_X7107BAC_246246 | OH
50 | 126 | 221 | 214 | SHE215_X4351ABC_5139435 | UG
51 | 238 | 143 | 54 | SHE215_Y1016ABC_401452 | OH
52 | 239 | 78 | 55 | SHE215_Y1002ABC_91469 | OH
52 | 202 | 185 | 160 | SHE215_Y1236A_91472 | OH
52 | 5 | 185 | 197 | SHE215_Y1345BAC_323436 | OH
53 | 97 | 111 | 56 | SHE215_X7057ABC_323474 | OH
54 | 102 | 110 | 57 | SHE215_Y1008ABC_91471 | OH
54 | 117 | 118 | 90 | SHE215_Y1207C_168960 | OH
55 | 14 | 200 | 58 | SHE215_Y1535BAC_246311 | OH
56 | 263 | 49 | 149 | SHE215_Y1431BAC_634053 | OH
56 | 34 | 158 | 59 | SHE215_Y1317BAC_88060 | OH
57 | 182 | 232 | 60 | SHE215_X7210A_556711 | OH
58 | 205 | 60 | 61 | SHE215_Y1186C_168968 | OH
59 | 136 | 53 | 62 | SHE215_X7087A_246251 | OH
59 | 198 | 196 | 206 | SHE215_X7139ACB_168976 | OH
60 | 187 | 20 | 63 | SHE215_X7470C_556721 | OH
61 | 179 | 78 | 212 | SHE215_S3P009A_5116913 | UG
61 | 148 | 96 | 278 | SHE215_Y1345BAC_634056 | OH
61 | 197 | 190 | 65 | SHE215_X7106BAC_168959 | OH
61 | 10 | 301 | 69 | SHE215_X4337BCA_478784 | OH
62 | 9 | 248 | 66 | SHE215_S3445ABC_5044600 | UG
63 | 241 | 350 | 67 | SHE215_X7091AC_479149 | OH
64 | 91 | 290 | 68 | SHE215_Y1533ACB_398751 | OH
65 | 93 | 87 | 70 | SHE215_Y1005A_91512 | OH
66 | 173 | 323 | 71 | SHE215_Y1313BAC_475799 | OH
67 | 189 | 172 | 72 | SHE215_Y1228ABC_323485 | UG
68 | 242 | 358 | 73 | SHE215_Y1321BAC_242842 | OH
69 | 17 | 196 | 74 | SHE215_X7461ABC_91130 | UG
70 | 167 | 258 | 76 | SHE215_X7449A_91475 | OH
71 | 15 | 212 | 78 | SHE215_Y1204CAB_246269 | OH
72 | 244 | 240 | 80 | SHE215_X4393BCA_401049 | OH
73 | 32 | 114 | 81 | SHE215_Y1415C_323445 | OH
73 | 114 | 231 | 94 | SHE215_Y1567CB_242864 | OH
74 | 148 | 121 | 82 | SHE215_Y1347BAC_401440 | OH
75 | 71 | 95 | 83 | SHE215_X7111BAC_168981 | OH
76 | 245 | 161 | 84 | SHE215_Y1421BAC_634024 | OH
77 | 198 | 184 | 85 | SHE215_Y1227BAC_246262 | OH
78 | 100 | 141 | 86 | SHE215_X7457C_634041 | OH
79 | 156 | 145 | 87 | SHE215_X7086BAC_323437 | OH
80 | 287 | 81 | 231 | SHE215_X7115B_245904 | UG
80 | 246 | 98 | 88 | SHE215_Y1407CAB_479172 | OH
81 | 199 | 111 | 89 | SHE215_Y1352ABC_4095261 | UG
82 | 8 | 167 | 91 | SHE215_Y1615BAC_88057 | OH
83 | 152 | 90 | 93 | SHE215_X7225BAC_401443 | OH
84 | 20 | 220 | 95 | SHE215_Y1387BAC_91476 | OH
85 | 141 | 198 | 96 | SHE215_Y1217BAC_91468 | OH
86 | 110 | 220 | 97 | SHE215_PB1785ABC_5044601 | UG
87 | 208 | 119 | 98 | SHE215_X7389ACB_556704 | OH
88 | 151 | 266 | 99 | SHE215_Y1352BAC_397882 | OH
89 | 247 | 212 | 101 | SHE215_Y1521C_246264 | OH
90 | 160 | 114 | 216 | SHE215_Y1590BAC_242844 | OH
90 | 248 | 219 | 102 | SHE215_Y1602ACB_5095972 | OH
91 | 249 | 98 | 103 | SHE215_Y1006ABC_479154 | OH
92 | 252 | 54 | 178 | SHE215_Y1318B_320019 | OH
92 | 250 | 71 | 104 | SHE215_X7088A_401444 | OH
93 | 295 | 139 | 274 | SHE215_Y1589BAC_166477 | OH
93 | 251 | 195 | 105 | SHE215_X7279ABC_91483 | OH
94 | 201 | 134 | 106 | SHE215_Y1362CAB_5066753 | UG
94 | 2 | 159 | 190 | SHE215_X7241BAC_634009 | OH
94 | 284 | 197 | 220 | SHE215_X7115BAC_91090 | OH
95 | 214 | 198 | 107 | SHE215_S3354CAB_5062765 | UG
96 | 149 | 72 | 151 | SHE215_X7389ACB_168973 | OH
96 | 139 | 116 | 108 | SHE215_Y1525BC_398767 | OH
97 | 9 | 61 | 109 | SHE215_Y1001ABC_246236 | OH
98 | 38 | 255 | 110 | SHE215_Y1497CAB_5062770 | UG
99 | 252 | 305 | 111 | SHE215_X7218BAC_246237 | OH
99 | 229 | 324 | 194 | SHE215_X4281BAC_633615 | OH
100 | 253 | 34 | 112 | SHE215_X7394AC_401453 | OH
101 | 255 | 300 | 114 | SHE215_X7490CAB_246241 | OH
102 | 107 | 125 | 115 | SHE215_X7468ABC_91474 | OH
103 | 27 | 187 | 236 | SHE215_Y1120C_401436 | OH
103 | 207 | 239 | 136 | SHE215_Y1015ABC_323439 | OH
103 | 30 | 245 | 116 | SHE215_X7003BCA_246295 | OH
104 | 36 | 102 | 117 | SHE215_X4365ACB_4054932 | OH
105 | 89 | 186 | 125 | SHE215_Y1415C_556712 | OH
105 | 256 | 315 | 118 | SHE215_Y1528CB_320004 | OH
106 | 79 | 176 | 119 | SHE215_Y1176A_401445 | OH
107 | 142 | 90 | 120 | SHE215_Y1537ABC_476674 | UG
108 | 175 | 98 | 121 | SHE215_Y1262BAC_323471 | OH
108 | 12 | 123 | 229 | SHE215_Y1497BAC_165601 | OH
109 | 221 | 205 | 122 | SHE215_Y1591BAC_553310 | OH
110 | 200 | 429 | 123 | SHE215_Y1262ABC_169003 | UG
111 | 82 | 100 | 138 | SHE215_Y1602ACB_556731 | OH
111 | 257 | 101 | 124 | SHE215_Y1123C_168975 | OH
112 | 258 | 104 | 126 | SHE215_Y1122C_556716 | OH
113 | 143 | 101 | 127 | SHE215_Y1240C_556717 | OH
114 | 68 | 80 | 128 | SHE215_Y1005ABC_168967 | OH
114 | 257 | 135 | 159 | SHE215_Y1021A_634030 | OH
115 | 195 | 177 | 129 | SHE215_X4338BCA_168624 | OH
116 | 259 | 225 | 130 | SHE215_X7129BAC_634012 | OH
116 | 91 | 257 | 280 | SHE215_Y1541BAC_320005 | OH
117 | 183 | 103 | 131 | SHE215_Y1614ABC_91520 | UG
118 | 191 | 169 | 132 | SHE215_S3441CAB_165635 | OH
118 | 274 | 321 | 174 | SHE215_Y1400BAC_398769 | OH
119 | 281 | 31 | 207 | SHE215_Y1423BAC_401476 | OH
119 | 260 | 170 | 133 | SHE215_X7002ABC_168995 | OH
120 | 254 | 180 | 215 | SHE215_Y1205C_634014 | OH
120 | 64 | 269 | 134 | SHE215_Y1589BAC_554181 | OH
121 | 46 | 99 | 135 | SHE215_X4336BCA_3789282 | OH
122 | 145 | 34 | 179 | SHE215_Y1542CAB_243716 | OH
122 | 261 | 103 | 137 | SHE215_S3P007A_5090157 | UG
123 | 171 | 131 | 139 | SHE215_X7461BAC_556326 | OH
124 | 74 | 93 | 140 | SHE215_S3354CAB_165634 | OH
124 | 49 | 159 | 263 | SHE215_X7511BAC_478764 | OH
125 | 106 | 20 | 156 | SHE215_X7487A_478793 | UG
125 | 178 | 81 | 141 | SHE215_S3120CAB_5044594 | OH
126 | 218 | 172 | 142 | SHE215_Y1022A_401496 | UG
127 | 209 | 178 | 143 | SHE215_Y1524BAC_88061 | OH
128 | 87 | 124 | 144 | SHE215_X7080BAC_91465 | OH
129 | 262 | 56 | 145 | SHE215_X7487BAC_91102 | OH
130 | 1 | 179 | 146 | SHE215_X7090A_91473 | OH
131 | 245 | 212 | 147 | SHE215_Y1223A_634011 | OH
132 | 161 | 163 | 148 | SHE215_X4601BCA_91119 | OH
133 | 264 | 25 | 150 | SHE215_Y1204BAC_479166 | OH
134 | 53 | 129 | 152 | SHE215_Y1253B_634069 | UG
135 | 181 | 136 | 153 | SHE215_S3120CAB_5044599 | OH
136 | 265 | 95 | 154 | SHE215_Y1385BAC_323452 | OH
137 | 266 | 158 | 155 | SHE215_X7111BCA_634036 | OH
137 | 267 | 228 | 158 | SHE215_Y1014ABC_246245 | OH
138 | 113 | 69 | 157 | SHE215_X7112BAC_91491 | OH
139 | 112 | 22 | 209 | SHE215_Y1123C_479161 | OH
139 | 269 | 150 | 162 | SHE215_X7442ABC_5091898 | UG
140 | 192 | 156 | 164 | SHE215_Y1530BAC_397856 | OH
141 | 270 | 201 | 165 | SHE215_X7P013B_91128 | UG
142 | 25 | 161 | 166 | SHE215_Y1020A_168974 | OH
143 | 164 | 174 | 167 | SHE215_X7108BAC_91509 | OH
144 | 196 | 115 | 271 | SHE215_X4001BCA_91112 | OH
144 | 271 | 124 | 168 | SHE215_X4132ACB_556354 | OH
145 | 272 | 146 | 169 | SHE215_Y1403BAC_242843 | OH
146 | 191 | 83 | 170 | SHE215_Y1536ACB_398761 | OH
146 | 293 | 418 | 265 | SHE215_X7279ABC_556713 | OH
147 | 78 | 187 | 171 | SHE215_Y1526CB_631498 | OH
148 | 273 | 136 | 172 | SHE215_Y1240C_479160 | OH
148 | 56 | 197 | 234 | SHE215_S3P006ABC_5090154 | UG
149 | 7 | 113 | 173 | SHE215_Y1227BAC_91515 | OH
150 | 67 | 40 | 223 | SHE215_X7068BAC_401437 | OH
150 | 275 | 107 | 175 | SHE215_X7069BAC_556709 | OH
150 | 85 | 159 | 272 | SHE215_Y1219BAC_246293 | OH
151 | 276 | 89 | 176 | SHE215_Y1362BAC_319999 | OH
151 | 279 | 159 | 232 | SHE215_Y1228BAC_91479 | OH
152 | 63 | 596 | 177 | SHE215_X7264ACB_323036 | OH
153 | 186 | 390 | 180 | SHE215_Y1004ABC_479158 | OH
154 | 86 | 80 | 192 | SHE215_X7P024ABC_5091899 | UG
154 | 272 | 108 | 182 | SHE215_Y1204CAB_323447 | OH
155 | 213 | 157 | 257 | SHE215_Y1251BAC_401477 | OH
155 | 277 | 341 | 183 | SHE215_Y1031ABC_246244 | OH
156 | 116 | 130 | 184 | SHE215_X4336ACB_556348 | OH
157 | 278 | 57 | 185 | SHE215_Y1527CB_165602 | OH
158 | 80 | 179 | 187 | SHE215_X7113BAC_246235 | OH
159 | 51 | 137 | 188 | SHE215_MH0259CAB_165641 | UG
160 | 94 | 60 | 261 | SHE215_X7215BAC_5026191 | OH
160 | 12 | 171 | 193 | SHE215_X7454C_401460 | OH
161 | 75 | 201 | 195 | SHE215_Y1387BAC_479202 | OH
162 | 99 | 138 | 196 | SHE215_Y1235A_246270 | OH
163 | 43 | 65 | 198 | SHE215_X7210A_556710 | OH
163 | 130 | 114 | 235 | SHE215_Y1542BAC_476621 | OH
164 | 279 | 166 | 199 | SHE215_X4630ABC_633644 | UG
165 | 280 | 67 | 200 | SHE215_X7002BAC_168964 | OH
166 | 140 | 147 | 201 | SHE215_X7442ABC_634015 | OH
167 | 157 | 81 | 202 | SHE215_X7115BAC_478763 | OH
167 | 26 | 271 | 275 | SHE215_X7089A_246252 | OH
168 | 6 | 248 | 203 | SHE215_X7130C_323442 | OH
169 | 133 | 181 | 204 | SHE215_X4363BCA_245896 | OH
169 | 290 | 213 | 277 | SHE215_X7118ABC_245905 | UG
170 | 47 | 125 | 205 | SHE215_X7489BAC_401055 | OH
171 | 176 | 38 | 208 | SHE215_X7109ABC_323478 | OH
172 | 24 | 484 | 210 | SHE215_Y1013A_246249 | OH
173 | 282 | 100 | 217 | SHE215_X4080CAB_91126 | OH
173 | 212 | 366 | 291 | SHE215_X7194C_323443 | OH
174 | 243 | 183 | 218 | SHE215_Y1007CA_246233 | OH
175 | 137 | 68 | 221 | SHE215_Y1588BAC_320891 | OH
175 | 211 | 276 | 294 | SHE215_Y1222A_634010 | OH
176 | 134 | 135 | 224 | SHE215_Y1P001B_246305 | UG
177 | 162 | 298 | 225 | SHE215_Y1611BAC_401485 | OH
178 | 261 | 1118 | 226 | SHE215_Y1118ABC_401442 | OH
179 | 285 | 58 | 227 | SHE215_Y1168B_246248 | OH
180 | 163 | 213 | 262 | SHE215_Y1216BAC_323460 | OH
180 | 101 | 317 | 228 | SHE215_Y1534ACB_320889 | OH
181 | 72 | 121 | 264 | SHE215_Y1185C_168970 | OH
181 | 286 | 159 | 230 | SHE215_PB1786ABC_5044602 | UG
182 | 288 | 161 | 233 | SHE215_Y1022A_246250 | OH
183 | 158 | 110 | 237 | SHE215_X7070BAC_246274 | OH
184 | 190 | 84 | 238 | SHE215_Y1351CAB_323457 | OH
185 | 214 | 236 | 239 | SHE215_Y1007CBA_323431 | OH
186 | 289 | 242 | 240 | SHE215_Y1385BAC_556732 | OH
187 | 186 | 240 | 241 | SHE215_X7454C_91467 | OH
188 | 155 | 168 | 243 | SHE215_Y1001ABC_634032 | OH
189 | 290 | 120 | 244 | SHE215_Y1235A_479157 | OH
190 | 268 | 91 | 245 | SHE215_Y1400ABC_398826 | UG
191 | 62 | 304 | 247 | SHE215_Y1242C_479159 | OH
192 | 159 | 133 | 248 | SHE215_Y1538BAC_554176 | OH
193 | 291 | 132 | 249 | SHE215_Y1039BAC_88059 | OH
194 | 90 | 92 | 250 | SHE215_Y1616ABC_91526 | UG
195 | 4 | 203 | 251 | SHE215_Y1039BAC_320002 | OH
196 | 292 | 124 | 252 | SHE215_Y1614B_323430 | OH
197 | 109 | 243 | 253 | SHE215_X4336BCA_168605 | OH
198 | 88 | 89 | 254 | SHE215_Y1419BAC_634002 | OH
199 | 239 | 76 | 255 | SHE215_X7449A_634016 | OH
200 | 172 | 408 | 256 | SHE215_X7108BAC_246247 | OH
201 | 58 | 177 | 259 | SHE215_X7498BAC_633608 | OH
202 | 96 | 74 | 266 | SHE215_X4132CAB_556328 | OH
202 | 296 | 232 | 283 | SHE215_X7068BAC_634058 | OH
203 | 59 | 166 | 267 | SHE215_X7092A_246238 | OH
204 | 120 | 130 | 268 | SHE215_Y1318BAC_242845 | OH
204 | 89 | 147 | 270 | SHE215_X4133BAC_168601 | OH
205 | 294 | 86 | 269 | SHE215_Y1175A_479156 | OH
206 | 35 | 130 | 273 | SHE215_Y1242C_323450 | OH
207 | 177 | 357 | 276 | SHE215_Y1252BAC_556715 | OH
208 | 65 | 113 | 279 | SHE215_X7265ACB_401459 | OH
209 | 169 | 206 | 281 | SHE215_Y1115A_323458 | OH
210 | 135 | 138 | 282 | SHE215_X4364BCA_5128806 | OH
211 | 37 | 273 | 284 | SHE215_Y1019CA_479170 | OH
212 | 8 | 368 | 285 | SHE215_Y1349CAB_479150 | OH
213 | 210 | 165 | 286 | SHE215_PB0754A_478794 | UG
214 | 57 | 84 | 287 | SHE215_X7264ACB_168958 | OH
215 | 166 | 114 | 288 | SHE215_X7212BAC_634007 | OH
216 | 297 | 314 | 289 | SHE215_X4601BCA_91117 | OH
217 | 298 | 429 | 290 | SHE215_Y1251BAC_479162 | OH
218 | 129 | 112 | 292 | SHE215_X7P004C_556743 | UG
219 | 299 | 210 | 295 | SHE215_Y1140C_323441 | OH
220 | 240 | 129 | 296 | SHE215_X4351BAC_556322 | OH
221 | 232 | 142 | 298 | SHE215_Y1248BAC_479152 | OH

## Configurations
Conf | Lin=1, Trafo=0 | R11 | R12 | R13 | R22 | R23 | R33 | X11 | X12 | X13 | X22 | X23 | X33 | B11 | B12 | B13 | B22 | B23 | B33
1 | 1 | 1.573 | 0.1641 | 0.1627 | 1.576 | 0.1641 | 1.573 | 1.293 | 0.5534 | 0.4726 | 1.286 | 0.5534 | 1.293 | 4.586 | -1.2 | -0.6579 | 4.826 | -1.2 | 4.586
2 | 1 | 1.051 | 0.1641 | 0.1627 | 1.054 | 0.1641 | 1.051 | 1.377 | 0.5534 | 0.4726 | 1.37 | 0.5534 | 1.377 | 4.807 | -1.302 | -0.7021 | 5.08 | -1.302 | 4.807
3 | 1 | 1.1166 | 0.21533 | 0.21533 | 1.1166 | 0.21533 | 1.1166 | 0.4029 | 0.0086996 | 0.0086996 | 0.4029 | 0.0086996 | 0.4029 | 33.2394 | -8.5519 | -8.5519 | 33.2394 | -8.5519 | 33.2394
4 | 1 | 1.1166 | 0.21533 | 0.21533 | 1.1166 | 0.21533 | 1.1166 | 0.4029 | 0.0086996 | 0.0086996 | 0.4029 | 0.0086996 | 0.4029 | 33.2394 | -8.5519 | -8.5519 | 33.2394 | -8.5519 | 33.2394
5 | 1 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0 | 0 | 0 | 0 | 0 | 1.379 | 0 | 0 | 0 | 0 | 0 | 4.217
6 | 1 | 1.048 | 0.1641 | 0.1627 | 1.051 | 0.1641 | 1.048 | 1.265 | 0.5534 | 0.4726 | 1.258 | 0.5534 | 1.265 | 4.749 | -1.275 | -0.6905 | 5.013 | -1.275 | 4.749
7 | 1 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0 | 0 | 0 | 0 | 0 | 1.379 | 0 | 0 | 0 | 0 | 0 | 4.217
8 | 1 | 1.1166 | 0.21533 | 0.21533 | 1.1166 | 0.21533 | 1.1166 | 0.4029 | 0.0086996 | 0.0086996 | 0.4029 | 0.0086996 | 0.4029 | 33.2394 | -8.5519 | -8.5519 | 33.2394 | -8.5519 | 33.2394
9 | 1 | 0.4406 | 0.1641 | 0.1627 | 0.4435 | 0.1641 | 0.4406 | 1.222 | 0.5534 | 0.4726 | 1.216 | 0.5534 | 1.222 | 5.02 | -1.405 | -0.7445 | 5.327 | -1.405 | 5.02
10 | 1 | 2.343 | 0.1641 | 0.1627 | 2.346 | 0.1641 | 2.343 | 1.356 | 0.5534 | 0.4726 | 1.349 | 0.5534 | 1.356 | 4.22 | -1.036 | -0.5843 | 4.411 | -1.036 | 4.22
11 | 1 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0 | 0 | 0 | 0 | 0 | 1.379 | 0 | 0 | 0 | 0 | 0 | 4.217
12 | 1 | 1.045 | 0.1641 | 0.1627 | 1.048 | 0.1641 | 1.045 | 1.293 | 0.5534 | 0.4726 | 1.286 | 0.5534 | 1.293 | 4.586 | -1.2 | -0.6579 | 4.826 | -1.2 | 4.586
13 | 1 | 0 | 0 | 0 | 0 | 0 | 1.1166 | 0 | 0 | 0 | 0 | 0 | 0.4029 | 0 | 0 | 0 | 0 | 0 | 33.2394
14 | 1 | 1.048 | 0.1641 | 0.1627 | 1.051 | 0.1641 | 1.048 | 1.265 | 0.5534 | 0.4726 | 1.258 | 0.5534 | 1.265 | 4.749 | -1.275 | -0.6905 | 5.013 | -1.275 | 4.749
15 | 1 | 2.343 | 0.1641 | 0.1627 | 2.346 | 0.1641 | 2.343 | 1.356 | 0.5534 | 0.4726 | 1.349 | 0.5534 | 1.356 | 4.22 | -1.036 | -0.5843 | 4.411 | -1.036 | 4.22
16 | 1 | 1.048 | 0.1641 | 0.1627 | 1.051 | 0.1641 | 1.048 | 1.265 | 0.5534 | 0.4726 | 1.258 | 0.5534 | 1.265 | 4.749 | -1.275 | -0.6905 | 5.013 | -1.275 | 4.749
17 | 1 | 0.6047 | 0.1641 | 0.1627 | 0.6076 | 0.1641 | 0.6047 | 1.222 | 0.5534 | 0.4726 | 1.216 | 0.5534 | 1.222 | 5.02 | -1.405 | -0.7445 | 5.327 | -1.405 | 5.02
18 | 1 | 1.048 | 0.1641 | 0.1627 | 1.051 | 0.1641 | 1.048 | 1.265 | 0.5534 | 0.4726 | 1.258 | 0.5534 | 1.265 | 4.749 | -1.275 | -0.6905 | 5.013 | -1.275 | 4.749
19 | 1 | 0.6047 | 0.1641 | 0.1627 | 0.6076 | 0.1641 | 0.6047 | 1.222 | 0.5534 | 0.4726 | 1.216 | 0.5534 | 1.222 | 5.02 | -1.405 | -0.7445 | 5.327 | -1.405 | 5.02
20 | 1 | 2.343 | 0 | 0.1627 | 0 | 0 | 2.343 | 1.356 | 0 | 0.4726 | 0 | 0 | 1.356 | 3.976 | 0 | -0.8276 | 0 | 0 | 3.976
21 | 1 | 1.1166 | 0.21533 | 0.21533 | 1.1166 | 0.21533 | 1.1166 | 0.4029 | 0.0086996 | 0.0086996 | 0.4029 | 0.0086996 | 0.4029 | 33.2394 | -8.5519 | -8.5519 | 33.2394 | -8.5519 | 33.2394
22 | 1 | 0.3327 | 0.1641 | 0.1627 | 0.3356 | 0.1641 | 0.3327 | 1.157 | 0.5534 | 0.4726 | 1.15 | 0.5534 | 1.157 | 5.465 | -1.627 | -0.8319 | 5.851 | -1.627 | 5.465
23 | 1 | 1.573 | 0.1641 | 0.1627 | 1.576 | 0.1641 | 1.573 | 1.293 | 0.5534 | 0.4726 | 1.286 | 0.5534 | 1.293 | 4.586 | -1.2 | -0.6579 | 4.826 | -1.2 | 4.586
24 | 1 | 1.1166 | 0.21533 | 0.21533 | 1.1166 | 0.21533 | 1.1166 | 0.4029 | 0.0086996 | 0.0086996 | 0.4029 | 0.0086996 | 0.4029 | 33.2394 | -8.5519 | -8.5519 | 33.2394 | -8.5519 | 33.2394
25 | 1 | 2.343 | 0.1641 | 0.1627 | 2.346 | 0.1641 | 2.343 | 1.356 | 0.5534 | 0.4726 | 1.349 | 0.5534 | 1.356 | 4.22 | -1.036 | -0.5843 | 4.411 | -1.036 | 4.22
26 | 1 | 0.3327 | 0.1641 | 0.1627 | 0.3356 | 0.1641 | 0.3327 | 1.157 | 0.5534 | 0.4726 | 1.15 | 0.5534 | 1.157 | 5.465 | -1.627 | -0.8319 | 5.851 | -1.627 | 5.465
27 | 1 | 1.573 | 0.1641 | 0.1627 | 1.576 | 0.1641 | 1.573 | 1.293 | 0.5534 | 0.4726 | 1.286 | 0.5534 | 1.293 | 4.586 | -1.2 | -0.6579 | 4.826 | -1.2 | 4.586
28 | 1 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0 | 0 | 0 | 0 | 0 | 1.379 | 0 | 0 | 0 | 0 | 0 | 4.217
29 | 1 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0 | 0 | 0 | 0 | 0 | 1.379 | 0 | 0 | 0 | 0 | 0 | 4.217
30 | 1 | 1.1166 | 0.21533 | 0.21533 | 1.1166 | 0.21533 | 1.1166 | 0.4029 | 0.0086996 | 0.0086996 | 0.4029 | 0.0086996 | 0.4029 | 33.2394 | -8.5519 | -8.5519 | 33.2394 | -8.5519 | 33.2394
31 | 1 | 2.343 | 0.1641 | 0.1627 | 2.346 | 0.1641 | 2.343 | 1.356 | 0.5534 | 0.4726 | 1.349 | 0.5534 | 1.356 | 4.22 | -1.036 | -0.5843 | 4.411 | -1.036 | 4.22
32 | 1 | 1.048 | 0.1641 | 0.1627 | 1.051 | 0.1641 | 1.048 | 1.265 | 0.5534 | 0.4726 | 1.258 | 0.5534 | 1.265 | 4.749 | -1.275 | -0.6905 | 5.013 | -1.275 | 4.749
33 | 1 | 1.048 | 0.1641 | 0.1627 | 1.051 | 0.1641 | 1.048 | 1.265 | 0.5534 | 0.4726 | 1.258 | 0.5534 | 1.265 | 4.749 | -1.275 | -0.6905 | 5.013 | -1.275 | 4.749
34 | 1 | 0.6047 | 0.1641 | 0.1627 | 0.6076 | 0.1641 | 0.6047 | 1.222 | 0.5534 | 0.4726 | 1.216 | 0.5534 | 1.222 | 5.02 | -1.405 | -0.7445 | 5.327 | -1.405 | 5.02
35 | 1 | 1.573 | 0.1641 | 0.1627 | 1.576 | 0.1641 | 1.573 | 1.293 | 0.5534 | 0.4726 | 1.286 | 0.5534 | 1.293 | 4.586 | -1.2 | -0.6579 | 4.826 | -1.2 | 4.586
36 | 1 | 1.573 | 0.1641 | 0.1627 | 1.576 | 0.1641 | 1.573 | 1.293 | 0.5534 | 0.4726 | 1.286 | 0.5534 | 1.293 | 4.586 | -1.2 | -0.6579 | 4.826 | -1.2 | 4.586
37 | 1 | 0.4406 | 0.1641 | 0.1627 | 0.4435 | 0.1641 | 0.4406 | 1.222 | 0.5534 | 0.4726 | 1.216 | 0.5534 | 1.222 | 5.02 | -1.405 | -0.7445 | 5.327 | -1.405 | 5.02
38 | 1 | 1.048 | 0.1641 | 0.1627 | 1.051 | 0.1641 | 1.048 | 1.265 | 0.5534 | 0.4726 | 1.258 | 0.5534 | 1.265 | 4.749 | -1.275 | -0.6905 | 5.013 | -1.275 | 4.749
39 | 1 | 2.343 | 0.1641 | 0.1627 | 2.346 | 0.1641 | 2.343 | 1.356 | 0.5534 | 0.4726 | 1.349 | 0.5534 | 1.356 | 4.22 | -1.036 | -0.5843 | 4.411 | -1.036 | 4.22
40 | 1 | 1.045 | 0.1641 | 0.1627 | 1.048 | 0.1641 | 1.045 | 1.293 | 0.5534 | 0.4726 | 1.286 | 0.5534 | 1.293 | 4.586 | -1.2 | -0.6579 | 4.826 | -1.2 | 4.586
41 | 1 | 1.045 | 0.1641 | 0.1627 | 1.048 | 0.1641 | 1.045 | 1.293 | 0.5534 | 0.4726 | 1.286 | 0.5534 | 1.293 | 4.586 | -1.2 | -0.6579 | 4.826 | -1.2 | 4.586
42 | 1 | 1.048 | 0.1641 | 0.1627 | 1.051 | 0.1641 | 1.048 | 1.265 | 0.5534 | 0.4726 | 1.258 | 0.5534 | 1.265 | 4.749 | -1.275 | -0.6905 | 5.013 | -1.275 | 4.749
43 | 1 | 1.1166 | 0.21533 | 0.21533 | 1.1166 | 0.21533 | 1.1166 | 0.4029 | 0.0086996 | 0.0086996 | 0.4029 | 0.0086996 | 0.4029 | 33.2394 | -8.5519 | -8.5519 | 33.2394 | -8.5519 | 33.2394
44 | 1 | 1.1166 | 0.21533 | 0.21533 | 1.1166 | 0.21533 | 1.1166 | 0.4029 | 0.0086996 | 0.0086996 | 0.4029 | 0.0086996 | 0.4029 | 33.2394 | -8.5519 | -8.5519 | 33.2394 | -8.5519 | 33.2394
45 | 1 | 1.047 | 0 | 0 | 0 | 0 | 0 | 1.267 | 0 | 0 | 0 | 0 | 0 | 4.176 | 0 | 0 | 0 | 0 | 0
46 | 1 | 1.048 | 0.1641 | 0.1627 | 1.051 | 0.1641 | 1.048 | 1.265 | 0.5534 | 0.4726 | 1.258 | 0.5534 | 1.265 | 4.749 | -1.275 | -0.6905 | 5.013 | -1.275 | 4.749
47 | 1 | 2.342 | 0 | 0 | 0 | 0 | 0 | 1.358 | 0 | 0 | 0 | 0 | 0 | 3.791 | 0 | 0 | 0 | 0 | 0
48 | 1 | 0.6047 | 0.1641 | 0.1627 | 0.6076 | 0.1641 | 0.6047 | 1.222 | 0.5534 | 0.4726 | 1.216 | 0.5534 | 1.222 | 5.02 | -1.405 | -0.7445 | 5.327 | -1.405 | 5.02
49 | 1 | 0.4406 | 0.1641 | 0.1627 | 0.4435 | 0.1641 | 0.4406 | 1.222 | 0.5534 | 0.4726 | 1.216 | 0.5534 | 1.222 | 5.02 | -1.405 | -0.7445 | 5.327 | -1.405 | 5.02
50 | 1 | 1.1166 | 0.21533 | 0.21533 | 1.1166 | 0.21533 | 1.1166 | 0.4029 | 0.0086996 | 0.0086996 | 0.4029 | 0.0086996 | 0.4029 | 33.2394 | -8.5519 | -8.5519 | 33.2394 | -8.5519 | 33.2394
51 | 1 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0 | 0 | 0 | 0 | 0 | 1.379 | 0 | 0 | 0 | 0 | 0 | 4.217
52 | 1 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0 | 0 | 0 | 0 | 0 | 1.379 | 0 | 0 | 0 | 0 | 0 | 4.217
53 | 1 | 0.6047 | 0.1641 | 0.1627 | 0.6076 | 0.1641 | 0.6047 | 1.222 | 0.5534 | 0.4726 | 1.216 | 0.5534 | 1.222 | 5.02 | -1.405 | -0.7445 | 5.327 | -1.405 | 5.02
54 | 1 | 1.05 | 0 | 0 | 0 | 0 | 0 | 1.379 | 0 | 0 | 0 | 0 | 0 | 4.217 | 0 | 0 | 0 | 0 | 0
55 | 1 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0 | 0 | 0 | 0 | 0 | 1.379 | 0 | 0 | 0 | 0 | 0 | 4.217
56 | 1 | 0 | 0 | 0 | 1.048 | 0.1627 | 1.048 | 0 | 0 | 0 | 1.265 | 0.4726 | 1.265 | 0 | 0 | 0 | 4.425 | -1.015 | 4.425
57 | 1 | 2.342 | 0 | 0 | 0 | 0 | 0 | 1.358 | 0 | 0 | 0 | 0 | 0 | 3.791 | 0 | 0 | 0 | 0 | 0
58 | 1 | 1.048 | 0.1641 | 0.1627 | 1.051 | 0.1641 | 1.048 | 1.265 | 0.5534 | 0.4726 | 1.258 | 0.5534 | 1.265 | 4.749 | -1.275 | -0.6905 | 5.013 | -1.275 | 4.749
59 | 1 | 0.6047 | 0.1641 | 0.1627 | 0.6076 | 0.1641 | 0.6047 | 1.222 | 0.5534 | 0.4726 | 1.216 | 0.5534 | 1.222 | 5.02 | -1.405 | -0.7445 | 5.327 | -1.405 | 5.02
60 | 1 | 1.048 | 0.1641 | 0.1627 | 1.051 | 0.1641 | 1.048 | 1.265 | 0.5534 | 0.4726 | 1.258 | 0.5534 | 1.265 | 4.749 | -1.275 | -0.6905 | 5.013 | -1.275 | 4.749
61 | 1 | 1.051 | 0.1641 | 0.1627 | 1.054 | 0.1641 | 1.051 | 1.377 | 0.5534 | 0.4726 | 1.37 | 0.5534 | 1.377 | 4.807 | -1.302 | -0.7021 | 5.08 | -1.302 | 4.807
62 | 1 | 1.048 | 0.1641 | 0.1627 | 1.051 | 0.1641 | 1.048 | 1.265 | 0.5534 | 0.4726 | 1.258 | 0.5534 | 1.265 | 4.749 | -1.275 | -0.6905 | 5.013 | -1.275 | 4.749
63 | 1 | 0.3327 | 0.1641 | 0.1627 | 0.3356 | 0.1641 | 0.3327 | 1.157 | 0.5534 | 0.4726 | 1.15 | 0.5534 | 1.157 | 5.465 | -1.627 | -0.8319 | 5.851 | -1.627 | 5.465
64 | 1 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0 | 0 | 0 | 0 | 0 | 1.379 | 0 | 0 | 0 | 0 | 0 | 4.217
65 | 1 | 0.4406 | 0.1641 | 0.1627 | 0.4435 | 0.1641 | 0.4406 | 1.222 | 0.5534 | 0.4726 | 1.216 | 0.5534 | 1.222 | 5.02 | -1.405 | -0.7445 | 5.327 | -1.405 | 5.02
66 | 1 | 0.4406 | 0.1641 | 0.1627 | 0.4435 | 0.1641 | 0.4406 | 1.222 | 0.5534 | 0.4726 | 1.216 | 0.5534 | 1.222 | 5.02 | -1.405 | -0.7445 | 5.327 | -1.405 | 5.02
67 | 1 | 1.1166 | 0.21533 | 0.21533 | 1.1166 | 0.21533 | 1.1166 | 0.4029 | 0.0086996 | 0.0086996 | 0.4029 | 0.0086996 | 0.4029 | 33.2394 | -8.5519 | -8.5519 | 33.2394 | -8.5519 | 33.2394
68 | 1 | 0.40063 | 0.21533 | 0.21533 | 0.40063 | 0.21533 | 0.40063 | 0.32307 | 0.0086669 | 0.0086669 | 0.32307 | 0.0086669 | 0.32307 | 52.5085 | -7.5843 | -7.5843 | 52.5085 | -7.5843 | 52.5085
69 | 1 | 0.3327 | 0.1641 | 0.1627 | 0.3356 | 0.1641 | 0.3327 | 1.157 | 0.5534 | 0.4726 | 1.15 | 0.5534 | 1.157 | 5.465 | -1.627 | -0.8319 | 5.851 | -1.627 | 5.465
70 | 1 | 1.572 | 0 | 0 | 0 | 0 | 0 | 1.294 | 0 | 0 | 0 | 0 | 0 | 4.06 | 0 | 0 | 0 | 0 | 0
71 | 1 | 2.343 | 0.1627 | 0 | 2.343 | 0 | 0 | 1.356 | 0.4726 | 0 | 1.356 | 0 | 0 | 3.976 | -0.8276 | 0 | 3.976 | 0 | 0
72 | 1 | 0.3327 | 0.1641 | 0.1627 | 0.3356 | 0.1641 | 0.3327 | 1.157 | 0.5534 | 0.4726 | 1.15 | 0.5534 | 1.157 | 5.465 | -1.627 | -0.8319 | 5.851 | -1.627 | 5.465
73 | 1 | 1.1166 | 0.21533 | 0.21533 | 1.1166 | 0.21533 | 1.1166 | 0.4029 | 0.0086996 | 0.0086996 | 0.4029 | 0.0086996 | 0.4029 | 33.2394 | -8.5519 | -8.5519 | 33.2394 | -8.5519 | 33.2394
74 | 1 | 0.6047 | 0.1641 | 0.1627 | 0.6076 | 0.1641 | 0.6047 | 1.222 | 0.5534 | 0.4726 | 1.216 | 0.5534 | 1.222 | 5.02 | -1.405 | -0.7445 | 5.327 | -1.405 | 5.02
75 | 1 | 0.4406 | 0.1641 | 0.1627 | 0.4435 | 0.1641 | 0.4406 | 1.222 | 0.5534 | 0.4726 | 1.216 | 0.5534 | 1.222 | 5.02 | -1.405 | -0.7445 | 5.327 | -1.405 | 5.02
76 | 1 | 0.3327 | 0.1641 | 0.1627 | 0.3356 | 0.1641 | 0.3327 | 1.157 | 0.5534 | 0.4726 | 1.15 | 0.5534 | 1.157 | 5.465 | -1.627 | -0.8319 | 5.851 | -1.627 | 5.465
77 | 1 | 1.1166 | 0.21533 | 0.21533 | 1.1166 | 0.21533 | 1.1166 | 0.4029 | 0.0086996 | 0.0086996 | 0.4029 | 0.0086996 | 0.4029 | 33.2394 | -8.5519 | -8.5519 | 33.2394 | -8.5519 | 33.2394
78 | 1 | 2.343 | 0.1641 | 0.1627 | 2.346 | 0.1641 | 2.343 | 1.356 | 0.5534 | 0.4726 | 1.349 | 0.5534 | 1.356 | 4.22 | -1.036 | -0.5843 | 4.411 | -1.036 | 4.22
79 | 1 | 2.343 | 0.1641 | 0.1627 | 2.346 | 0.1641 | 2.343 | 1.356 | 0.5534 | 0.4726 | 1.349 | 0.5534 | 1.356 | 4.22 | -1.036 | -0.5843 | 4.411 | -1.036 | 4.22
80 | 1 | 2.342 | 0 | 0 | 0 | 0 | 0 | 1.358 | 0 | 0 | 0 | 0 | 0 | 3.791 | 0 | 0 | 0 | 0 | 0
81 | 1 | 1.048 | 0.1641 | 0.1627 | 1.051 | 0.1641 | 1.048 | 1.265 | 0.5534 | 0.4726 | 1.258 | 0.5534 | 1.265 | 4.749 | -1.275 | -0.6905 | 5.013 | -1.275 | 4.749
82 | 1 | 1.048 | 0.1641 | 0.1627 | 1.051 | 0.1641 | 1.048 | 1.265 | 0.5534 | 0.4726 | 1.258 | 0.5534 | 1.265 | 4.749 | -1.275 | -0.6905 | 5.013 | -1.275 | 4.749
83 | 1 | 2.343 | 0.1641 | 0.1627 | 2.346 | 0.1641 | 2.343 | 1.356 | 0.5534 | 0.4726 | 1.349 | 0.5534 | 1.356 | 4.22 | -1.036 | -0.5843 | 4.411 | -1.036 | 4.22
84 | 1 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0 | 0 | 0 | 0 | 0 | 1.379 | 0 | 0 | 0 | 0 | 0 | 4.217
85 | 1 | 1.048 | 0.1641 | 0.1627 | 1.051 | 0.1641 | 1.048 | 1.265 | 0.5534 | 0.4726 | 1.258 | 0.5534 | 1.265 | 4.749 | -1.275 | -0.6905 | 5.013 | -1.275 | 4.749
86 | 1 | 1.051 | 0.1641 | 0.1627 | 1.054 | 0.1641 | 1.051 | 1.377 | 0.5534 | 0.4726 | 1.37 | 0.5534 | 1.377 | 4.807 | -1.302 | -0.7021 | 5.08 | -1.302 | 4.807
87 | 1 | 0.6047 | 0.1641 | 0.1627 | 0.6076 | 0.1641 | 0.6047 | 1.222 | 0.5534 | 0.4726 | 1.216 | 0.5534 | 1.222 | 5.02 | -1.405 | -0.7445 | 5.327 | -1.405 | 5.02
88 | 1 | 2.342 | 0 | 0 | 0 | 0 | 0 | 1.358 | 0 | 0 | 0 | 0 | 0 | 3.791 | 0 | 0 | 0 | 0 | 0
89 | 1 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0 | 0 | 0 | 0 | 0 | 1.379 | 0 | 0 | 0 | 0 | 0 | 4.217
90 | 1 | 2.342 | 0 | 0 | 0 | 0 | 0 | 1.358 | 0 | 0 | 0 | 0 | 0 | 3.791 | 0 | 0 | 0 | 0 | 0
91 | 1 | 1.048 | 0.1641 | 0.1627 | 1.051 | 0.1641 | 1.048 | 1.265 | 0.5534 | 0.4726 | 1.258 | 0.5534 | 1.265 | 4.749 | -1.275 | -0.6905 | 5.013 | -1.275 | 4.749
92 | 1 | 0 | 0 | 0 | 0 | 0 | 1.572 | 0 | 0 | 0 | 0 | 0 | 1.294 | 0 | 0 | 0 | 0 | 0 | 4.06
93 | 1 | 1.1166 | 0.21533 | 0.21533 | 1.1166 | 0.21533 | 1.1166 | 0.4029 | 0.0086996 | 0.0086996 | 0.4029 | 0.0086996 | 0.4029 | 33.2394 | -8.5519 | -8.5519 | 33.2394 | -8.5519 | 33.2394
94 | 1 | 1.048 | 0.1641 | 0.1627 | 1.051 | 0.1641 | 1.048 | 1.265 | 0.5534 | 0.4726 | 1.258 | 0.5534 | 1.265 | 4.749 | -1.275 | -0.6905 | 5.013 | -1.275 | 4.749
95 | 1 | 0.3327 | 0.1641 | 0.1627 | 0.3356 | 0.1641 | 0.3327 | 1.157 | 0.5534 | 0.4726 | 1.15 | 0.5534 | 1.157 | 5.465 | -1.627 | -0.8319 | 5.851 | -1.627 | 5.465
96 | 1 | 1.048 | 0.1641 | 0.1627 | 1.051 | 0.1641 | 1.048 | 1.265 | 0.5534 | 0.4726 | 1.258 | 0.5534 | 1.265 | 4.749 | -1.275 | -0.6905 | 5.013 | -1.275 | 4.749
97 | 1 | 0.67363 | 0.21533 | 0.21533 | 0.67363 | 0.21533 | 0.67363 | 0.36027 | 0.0086669 | 0.0086669 | 0.36027 | 0.0086669 | 0.36027 | 44.1993 | -6.3841 | -6.3841 | 44.1993 | -6.3841 | 44.1993
98 | 1 | 2.343 | 0 | 0.1627 | 0 | 0 | 2.343 | 1.356 | 0 | 0.4726 | 0 | 0 | 1.356 | 3.976 | 0 | -0.8276 | 0 | 0 | 3.976
99 | 1 | 1.048 | 0.1641 | 0.1627 | 1.051 | 0.1641 | 1.048 | 1.265 | 0.5534 | 0.4726 | 1.258 | 0.5534 | 1.265 | 4.749 | -1.275 | -0.6905 | 5.013 | -1.275 | 4.749
100 | 1 | 1.047 | 0 | 0 | 0 | 0 | 0 | 1.267 | 0 | 0 | 0 | 0 | 0 | 4.176 | 0 | 0 | 0 | 0 | 0
101 | 1 | 0.6047 | 0.1641 | 0.1627 | 0.6076 | 0.1641 | 0.6047 | 1.222 | 0.5534 | 0.4726 | 1.216 | 0.5534 | 1.222 | 5.02 | -1.405 | -0.7445 | 5.327 | -1.405 | 5.02
102 | 1 | 1.1166 | 0.21533 | 0.21533 | 1.1166 | 0.21533 | 1.1166 | 0.4029 | 0.0086996 | 0.0086996 | 0.4029 | 0.0086996 | 0.4029 | 33.2394 | -8.5519 | -8.5519 | 33.2394 | -8.5519 | 33.2394
103 | 1 | 1.048 | 0.1641 | 0.1627 | 1.051 | 0.1641 | 1.048 | 1.265 | 0.5534 | 0.4726 | 1.258 | 0.5534 | 1.265 | 4.749 | -1.275 | -0.6905 | 5.013 | -1.275 | 4.749
104 | 1 | 1.1166 | 0.21533 | 0.21533 | 1.1166 | 0.21533 | 1.1166 | 0.4029 | 0.0086996 | 0.0086996 | 0.4029 | 0.0086996 | 0.4029 | 33.2394 | -8.5519 | -8.5519 | 33.2394 | -8.5519 | 33.2394
105 | 1 | 1.572 | 0 | 0 | 0 | 0 | 0 | 1.294 | 0 | 0 | 0 | 0 | 0 | 4.06 | 0 | 0 | 0 | 0 | 0
106 | 1 | 1.573 | 0.1641 | 0.1627 | 1.576 | 0.1641 | 1.573 | 1.293 | 0.5534 | 0.4726 | 1.286 | 0.5534 | 1.293 | 4.586 | -1.2 | -0.6579 | 4.826 | -1.2 | 4.586
107 | 1 | 1.048 | 0.1641 | 0.1627 | 1.051 | 0.1641 | 1.048 | 1.265 | 0.5534 | 0.4726 | 1.258 | 0.5534 | 1.265 | 4.749 | -1.275 | -0.6905 | 5.013 | -1.275 | 4.749
108 | 1 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0 | 0 | 0 | 0 | 0 | 1.379 | 0 | 0 | 0 | 0 | 0 | 4.217
109 | 1 | 0 | 0 | 0 | 1.048 | 0.1627 | 1.048 | 0 | 0 | 0 | 1.265 | 0.4726 | 1.265 | 0 | 0 | 0 | 4.425 | -1.015 | 4.425
110 | 1 | 1.048 | 0.1641 | 0.1627 | 1.051 | 0.1641 | 1.048 | 1.265 | 0.5534 | 0.4726 | 1.258 | 0.5534 | 1.265 | 4.749 | -1.275 | -0.6905 | 5.013 | -1.275 | 4.749
111 | 1 | 1.048 | 0.1641 | 0.1627 | 1.051 | 0.1641 | 1.048 | 1.265 | 0.5534 | 0.4726 | 1.258 | 0.5534 | 1.265 | 4.749 | -1.275 | -0.6905 | 5.013 | -1.275 | 4.749
112 | 1 | 1.573 | 0.1641 | 0.1627 | 1.576 | 0.1641 | 1.573 | 1.293 | 0.5534 | 0.4726 | 1.286 | 0.5534 | 1.293 | 4.586 | -1.2 | -0.6579 | 4.826 | -1.2 | 4.586
113 | 1 | 0.4406 | 0.1641 | 0.1627 | 0.4435 | 0.1641 | 0.4406 | 1.222 | 0.5534 | 0.4726 | 1.216 | 0.5534 | 1.222 | 5.02 | -1.405 | -0.7445 | 5.327 | -1.405 | 5.02
114 | 1 | 0 | 0 | 0 | 0 | 0 | 1.047 | 0 | 0 | 0 | 0 | 0 | 1.267 | 0 | 0 | 0 | 0 | 0 | 4.176
115 | 1 | 2.343 | 0.1641 | 0.1627 | 2.346 | 0.1641 | 2.343 | 1.356 | 0.5534 | 0.4726 | 1.349 | 0.5534 | 1.356 | 4.22 | -1.036 | -0.5843 | 4.411 | -1.036 | 4.22
116 | 1 | 1.1166 | 0.21533 | 0.21533 | 1.1166 | 0.21533 | 1.1166 | 0.4029 | 0.0086996 | 0.0086996 | 0.4029 | 0.0086996 | 0.4029 | 33.2394 | -8.5519 | -8.5519 | 33.2394 | -8.5519 | 33.2394
117 | 1 | 1.045 | 0.1641 | 0.1627 | 1.048 | 0.1641 | 1.045 | 1.293 | 0.5534 | 0.4726 | 1.286 | 0.5534 | 1.293 | 4.586 | -1.2 | -0.6579 | 4.826 | -1.2 | 4.586
118 | 1 | 1.1166 | 0.21533 | 0.21533 | 1.1166 | 0.21533 | 1.1166 | 0.4029 | 0.0086996 | 0.0086996 | 0.4029 | 0.0086996 | 0.4029 | 33.2394 | -8.5519 | -8.5519 | 33.2394 | -8.5519 | 33.2394
119 | 1 | 0.6047 | 0.1641 | 0.1627 | 0.6076 | 0.1641 | 0.6047 | 1.222 | 0.5534 | 0.4726 | 1.216 | 0.5534 | 1.222 | 5.02 | -1.405 | -0.7445 | 5.327 | -1.405 | 5.02
120 | 1 | 2.343 | 0.1641 | 0.1627 | 2.346 | 0.1641 | 2.343 | 1.356 | 0.5534 | 0.4726 | 1.349 | 0.5534 | 1.356 | 4.22 | -1.036 | -0.5843 | 4.411 | -1.036 | 4.22
121 | 1 | 0.4406 | 0.1641 | 0.1627 | 0.4435 | 0.1641 | 0.4406 | 1.222 | 0.5534 | 0.4726 | 1.216 | 0.5534 | 1.222 | 5.02 | -1.405 | -0.7445 | 5.327 | -1.405 | 5.02
122 | 1 | 0.4406 | 0.1641 | 0.1627 | 0.4435 | 0.1641 | 0.4406 | 1.222 | 0.5534 | 0.4726 | 1.216 | 0.5534 | 1.222 | 5.02 | -1.405 | -0.7445 | 5.327 | -1.405 | 5.02
123 | 1 | 0.67363 | 0.21533 | 0.21533 | 0.67363 | 0.21533 | 0.67363 | 0.36027 | 0.0086669 | 0.0086669 | 0.36027 | 0.0086669 | 0.36027 | 44.1993 | -6.3841 | -6.3841 | 44.1993 | -6.3841 | 44.1993
124 | 1 | 1.048 | 0.1641 | 0.1627 | 1.051 | 0.1641 | 1.048 | 1.265 | 0.5534 | 0.4726 | 1.258 | 0.5534 | 1.265 | 4.749 | -1.275 | -0.6905 | 5.013 | -1.275 | 4.749
125 | 1 | 1.051 | 0.1641 | 0.1627 | 1.054 | 0.1641 | 1.051 | 1.377 | 0.5534 | 0.4726 | 1.37 | 0.5534 | 1.377 | 4.807 | -1.302 | -0.7021 | 5.08 | -1.302 | 4.807
126 | 1 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0 | 0 | 0 | 0 | 0 | 1.379 | 0 | 0 | 0 | 0 | 0 | 4.217
127 | 1 | 1.048 | 0.1641 | 0.1627 | 1.051 | 0.1641 | 1.048 | 1.265 | 0.5534 | 0.4726 | 1.258 | 0.5534 | 1.265 | 4.749 | -1.275 | -0.6905 | 5.013 | -1.275 | 4.749
128 | 1 | 1.051 | 0.1641 | 0.1627 | 1.054 | 0.1641 | 1.051 | 1.377 | 0.5534 | 0.4726 | 1.37 | 0.5534 | 1.377 | 4.807 | -1.302 | -0.7021 | 5.08 | -1.302 | 4.807
129 | 1 | 2.343 | 0.1641 | 0.1627 | 2.346 | 0.1641 | 2.343 | 1.356 | 0.5534 | 0.4726 | 1.349 | 0.5534 | 1.356 | 4.22 | -1.036 | -0.5843 | 4.411 | -1.036 | 4.22
130 | 1 | 0 | 0 | 0 | 1.572 | 0 | 0 | 0 | 0 | 0 | 1.294 | 0 | 0 | 0 | 0 | 0 | 4.06 | 0 | 0
131 | 1 | 2.342 | 0 | 0 | 0 | 0 | 0 | 1.358 | 0 | 0 | 0 | 0 | 0 | 3.791 | 0 | 0 | 0 | 0 | 0
132 | 1 | 0.3327 | 0.1641 | 0.1627 | 0.3356 | 0.1641 | 0.3327 | 1.157 | 0.5534 | 0.4726 | 1.15 | 0.5534 | 1.157 | 5.465 | -1.627 | -0.8319 | 5.851 | -1.627 | 5.465
133 | 1 | 1.573 | 0.1641 | 0.1627 | 1.576 | 0.1641 | 1.573 | 1.293 | 0.5534 | 0.4726 | 1.286 | 0.5534 | 1.293 | 4.586 | -1.2 | -0.6579 | 4.826 | -1.2 | 4.586
134 | 1 | 0.40063 | 0.21533 | 0.21533 | 0.40063 | 0.21533 | 0.40063 | 0.32307 | 0.0086669 | 0.0086669 | 0.32307 | 0.0086669 | 0.32307 | 52.5085 | -7.5843 | -7.5843 | 52.5085 | -7.5843 | 52.5085
135 | 1 | 0.6047 | 0.1641 | 0.1627 | 0.6076 | 0.1641 | 0.6047 | 1.222 | 0.5534 | 0.4726 | 1.216 | 0.5534 | 1.222 | 5.02 | -1.405 | -0.7445 | 5.327 | -1.405 | 5.02
136 | 1 | 0.3327 | 0.1641 | 0.1627 | 0.3356 | 0.1641 | 0.3327 | 1.157 | 0.5534 | 0.4726 | 1.15 | 0.5534 | 1.157 | 5.465 | -1.627 | -0.8319 | 5.851 | -1.627 | 5.465
137 | 1 | 0.40063 | 0.21533 | 0.21533 | 0.40063 | 0.21533 | 0.40063 | 0.32307 | 0.0086669 | 0.0086669 | 0.32307 | 0.0086669 | 0.32307 | 52.5085 | -7.5843 | -7.5843 | 52.5085 | -7.5843 | 52.5085
138 | 1 | 1.048 | 0.1641 | 0.1627 | 1.051 | 0.1641 | 1.048 | 1.265 | 0.5534 | 0.4726 | 1.258 | 0.5534 | 1.265 | 4.749 | -1.275 | -0.6905 | 5.013 | -1.275 | 4.749
139 | 1 | 0 | 0 | 0 | 1.048 | 0.1627 | 1.048 | 0 | 0 | 0 | 1.265 | 0.4726 | 1.265 | 0 | 0 | 0 | 4.425 | -1.015 | 4.425
140 | 1 | 1.048 | 0.1641 | 0.1627 | 1.051 | 0.1641 | 1.048 | 1.265 | 0.5534 | 0.4726 | 1.258 | 0.5534 | 1.265 | 4.749 | -1.275 | -0.6905 | 5.013 | -1.275 | 4.749
141 | 1 | 0.40063 | 0.21533 | 0.21533 | 0.40063 | 0.21533 | 0.40063 | 0.32307 | 0.0086669 | 0.0086669 | 0.32307 | 0.0086669 | 0.32307 | 52.5085 | -7.5843 | -7.5843 | 52.5085 | -7.5843 | 52.5085
142 | 1 | 1.048 | 0.1641 | 0.1627 | 1.051 | 0.1641 | 1.048 | 1.265 | 0.5534 | 0.4726 | 1.258 | 0.5534 | 1.265 | 4.749 | -1.275 | -0.6905 | 5.013 | -1.275 | 4.749
143 | 1 | 0.3327 | 0.1641 | 0.1627 | 0.3356 | 0.1641 | 0.3327 | 1.157 | 0.5534 | 0.4726 | 1.15 | 0.5534 | 1.157 | 5.465 | -1.627 | -0.8319 | 5.851 | -1.627 | 5.465
144 | 1 | 2.343 | 0 | 0.1627 | 0 | 0 | 2.343 | 1.356 | 0 | 0.4726 | 0 | 0 | 1.356 | 3.976 | 0 | -0.8276 | 0 | 0 | 3.976
145 | 1 | 1.048 | 0.1641 | 0.1627 | 1.051 | 0.1641 | 1.048 | 1.265 | 0.5534 | 0.4726 | 1.258 | 0.5534 | 1.265 | 4.749 | -1.275 | -0.6905 | 5.013 | -1.275 | 4.749
146 | 1 | 1.573 | 0.1641 | 0.1627 | 1.576 | 0.1641 | 1.573 | 1.293 | 0.5534 | 0.4726 | 1.286 | 0.5534 | 1.293 | 4.586 | -1.2 | -0.6579 | 4.826 | -1.2 | 4.586
147 | 1 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0 | 0 | 0 | 0 | 0 | 1.379 | 0 | 0 | 0 | 0 | 0 | 4.217
148 | 1 | 2.343 | 0.1641 | 0.1627 | 2.346 | 0.1641 | 2.343 | 1.356 | 0.5534 | 0.4726 | 1.349 | 0.5534 | 1.356 | 4.22 | -1.036 | -0.5843 | 4.411 | -1.036 | 4.22
149 | 1 | 2.343 | 0.1641 | 0.1627 | 2.346 | 0.1641 | 2.343 | 1.356 | 0.5534 | 0.4726 | 1.349 | 0.5534 | 1.356 | 4.22 | -1.036 | -0.5843 | 4.411 | -1.036 | 4.22
150 | 1 | 1.048 | 0.1641 | 0.1627 | 1.051 | 0.1641 | 1.048 | 1.265 | 0.5534 | 0.4726 | 1.258 | 0.5534 | 1.265 | 4.749 | -1.275 | -0.6905 | 5.013 | -1.275 | 4.749
151 | 1 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0 | 0 | 0 | 0 | 0 | 1.379 | 0 | 0 | 0 | 0 | 0 | 4.217
152 | 1 | 0 | 0 | 0 | 1.048 | 0.1627 | 1.048 | 0 | 0 | 0 | 1.265 | 0.4726 | 1.265 | 0 | 0 | 0 | 4.425 | -1.015 | 4.425
153 | 1 | 2.342 | 0 | 0 | 0 | 0 | 0 | 1.358 | 0 | 0 | 0 | 0 | 0 | 3.791 | 0 | 0 | 0 | 0 | 0
154 | 1 | 1.1166 | 0.21533 | 0.21533 | 1.1166 | 0.21533 | 1.1166 | 0.4029 | 0.0086996 | 0.0086996 | 0.4029 | 0.0086996 | 0.4029 | 33.2394 | -8.5519 | -8.5519 | 33.2394 | -8.5519 | 33.2394
155 | 1 | 1.051 | 0.1641 | 0.1627 | 1.054 | 0.1641 | 1.051 | 1.377 | 0.5534 | 0.4726 | 1.37 | 0.5534 | 1.377 | 4.807 | -1.302 | -0.7021 | 5.08 | -1.302 | 4.807
156 | 1 | 0.6047 | 0.1641 | 0.1627 | 0.6076 | 0.1641 | 0.6047 | 1.222 | 0.5534 | 0.4726 | 1.216 | 0.5534 | 1.222 | 5.02 | -1.405 | -0.7445 | 5.327 | -1.405 | 5.02
157 | 1 | 1.048 | 0.1641 | 0.1627 | 1.051 | 0.1641 | 1.048 | 1.265 | 0.5534 | 0.4726 | 1.258 | 0.5534 | 1.265 | 4.749 | -1.275 | -0.6905 | 5.013 | -1.275 | 4.749
158 | 1 | 1.1166 | 0.21533 | 0.21533 | 1.1166 | 0.21533 | 1.1166 | 0.4029 | 0.0086996 | 0.0086996 | 0.4029 | 0.0086996 | 0.4029 | 33.2394 | -8.5519 | -8.5519 | 33.2394 | -8.5519 | 33.2394
159 | 1 | 1.048 | 0.1641 | 0.1627 | 1.051 | 0.1641 | 1.048 | 1.265 | 0.5534 | 0.4726 | 1.258 | 0.5534 | 1.265 | 4.749 | -1.275 | -0.6905 | 5.013 | -1.275 | 4.749
160 | 1 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0 | 0 | 0 | 0 | 0 | 1.379 | 0 | 0 | 0 | 0 | 0 | 4.217
161 | 1 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0 | 0 | 0 | 0 | 0 | 1.379 | 0 | 0 | 0 | 0 | 0 | 4.217
162 | 1 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0 | 0 | 0 | 0 | 0 | 1.379 | 0 | 0 | 0 | 0 | 0 | 4.217
163 | 1 | 2.343 | 0.1641 | 0.1627 | 2.346 | 0.1641 | 2.343 | 1.356 | 0.5534 | 0.4726 | 1.349 | 0.5534 | 1.356 | 4.22 | -1.036 | -0.5843 | 4.411 | -1.036 | 4.22
164 | 1 | 2.342 | 0 | 0 | 0 | 0 | 0 | 1.358 | 0 | 0 | 0 | 0 | 0 | 3.791 | 0 | 0 | 0 | 0 | 0
165 | 1 | 1.048 | 0.1641 | 0.1627 | 1.051 | 0.1641 | 1.048 | 1.265 | 0.5534 | 0.4726 | 1.258 | 0.5534 | 1.265 | 4.749 | -1.275 | -0.6905 | 5.013 | -1.275 | 4.749
166 | 1 | 2.343 | 0.1641 | 0.1627 | 2.346 | 0.1641 | 2.343 | 1.356 | 0.5534 | 0.4726 | 1.349 | 0.5534 | 1.356 | 4.22 | -1.036 | -0.5843 | 4.411 | -1.036 | 4.22
167 | 1 | 1.048 | 0.1641 | 0.1627 | 1.051 | 0.1641 | 1.048 | 1.265 | 0.5534 | 0.4726 | 1.258 | 0.5534 | 1.265 | 4.749 | -1.275 | -0.6905 | 5.013 | -1.275 | 4.749
168 | 1 | 1.1166 | 0.21533 | 0.21533 | 1.1166 | 0.21533 | 1.1166 | 0.4029 | 0.0086996 | 0.0086996 | 0.4029 | 0.0086996 | 0.4029 | 33.2394 | -8.5519 | -8.5519 | 33.2394 | -8.5519 | 33.2394
169 | 1 | 0.6047 | 0.1641 | 0.1627 | 0.6076 | 0.1641 | 0.6047 | 1.222 | 0.5534 | 0.4726 | 1.216 | 0.5534 | 1.222 | 5.02 | -1.405 | -0.7445 | 5.327 | -1.405 | 5.02
170 | 1 | 1.048 | 0.1641 | 0.1627 | 1.051 | 0.1641 | 1.048 | 1.265 | 0.5534 | 0.4726 | 1.258 | 0.5534 | 1.265 | 4.749 | -1.275 | -0.6905 | 5.013 | -1.275 | 4.749
171 | 1 | 1.051 | 0.1641 | 0.1627 | 1.054 | 0.1641 | 1.051 | 1.377 | 0.5534 | 0.4726 | 1.37 | 0.5534 | 1.377 | 4.807 | -1.302 | -0.7021 | 5.08 | -1.302 | 4.807
172 | 1 | 1.048 | 0.1641 | 0.1627 | 1.051 | 0.1641 | 1.048 | 1.265 | 0.5534 | 0.4726 | 1.258 | 0.5534 | 1.265 | 4.749 | -1.275 | -0.6905 | 5.013 | -1.275 | 4.749
173 | 1 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0 | 0 | 0 | 0 | 0 | 1.379 | 0 | 0 | 0 | 0 | 0 | 4.217
174 | 1 | 0.3327 | 0.1641 | 0.1627 | 0.3356 | 0.1641 | 0.3327 | 1.157 | 0.5534 | 0.4726 | 1.15 | 0.5534 | 1.157 | 5.465 | -1.627 | -0.8319 | 5.851 | -1.627 | 5.465
175 | 1 | 1.048 | 0.1641 | 0.1627 | 1.051 | 0.1641 | 1.048 | 1.265 | 0.5534 | 0.4726 | 1.258 | 0.5534 | 1.265 | 4.749 | -1.275 | -0.6905 | 5.013 | -1.275 | 4.749
176 | 1 | 1.573 | 0.1641 | 0.1627 | 1.576 | 0.1641 | 1.573 | 1.293 | 0.5534 | 0.4726 | 1.286 | 0.5534 | 1.293 | 4.586 | -1.2 | -0.6579 | 4.826 | -1.2 | 4.586
177 | 1 | 1.1166 | 0.21533 | 0.21533 | 1.1166 | 0.21533 | 1.1166 | 0.4029 | 0.0086996 | 0.0086996 | 0.4029 | 0.0086996 | 0.4029 | 33.2394 | -8.5519 | -8.5519 | 33.2394 | -8.5519 | 33.2394
178 | 1 | 1.048 | 0.1641 | 0.1627 | 1.051 | 0.1641 | 1.048 | 1.265 | 0.5534 | 0.4726 | 1.258 | 0.5534 | 1.265 | 4.749 | -1.275 | -0.6905 | 5.013 | -1.275 | 4.749
179 | 1 | 0.6047 | 0.1641 | 0.1627 | 0.6076 | 0.1641 | 0.6047 | 1.222 | 0.5534 | 0.4726 | 1.216 | 0.5534 | 1.222 | 5.02 | -1.405 | -0.7445 | 5.327 | -1.405 | 5.02
180 | 1 | 0.3327 | 0.1641 | 0.1627 | 0.3356 | 0.1641 | 0.3327 | 1.157 | 0.5534 | 0.4726 | 1.15 | 0.5534 | 1.157 | 5.465 | -1.627 | -0.8319 | 5.851 | -1.627 | 5.465
181 | 1 | 1.1166 | 0.21533 | 0.21533 | 1.1166 | 0.21533 | 1.1166 | 0.4029 | 0.0086996 | 0.0086996 | 0.4029 | 0.0086996 | 0.4029 | 33.2394 | -8.5519 | -8.5519 | 33.2394 | -8.5519 | 33.2394
182 | 1 | 0.6047 | 0.1641 | 0.1627 | 0.6076 | 0.1641 | 0.6047 | 1.222 | 0.5534 | 0.4726 | 1.216 | 0.5534 | 1.222 | 5.02 | -1.405 | -0.7445 | 5.327 | -1.405 | 5.02
183 | 1 | 1.1166 | 0 | 0 | 0 | 0 | 0 | 0.4029 | 0 | 0 | 0 | 0 | 0 | 33.2394 | 0 | 0 | 0 | 0 | 0
184 | 1 | 0.6047 | 0.1641 | 0.1627 | 0.6076 | 0.1641 | 0.6047 | 1.222 | 0.5534 | 0.4726 | 1.216 | 0.5534 | 1.222 | 5.02 | -1.405 | -0.7445 | 5.327 | -1.405 | 5.02
185 | 1 | 1.573 | 0.1641 | 0.1627 | 1.576 | 0.1641 | 1.573 | 1.293 | 0.5534 | 0.4726 | 1.286 | 0.5534 | 1.293 | 4.586 | -1.2 | -0.6579 | 4.826 | -1.2 | 4.586
186 | 1 | 0.3327 | 0.1641 | 0.1627 | 0.3356 | 0.1641 | 0.3327 | 1.157 | 0.5534 | 0.4726 | 1.15 | 0.5534 | 1.157 | 5.465 | -1.627 | -0.8319 | 5.851 | -1.627 | 5.465
187 | 1 | 2.342 | 0 | 0 | 0 | 0 | 0 | 1.358 | 0 | 0 | 0 | 0 | 0 | 3.791 | 0 | 0 | 0 | 0 | 0
188 | 1 | 2.342 | 0 | 0 | 0 | 0 | 0 | 1.358 | 0 | 0 | 0 | 0 | 0 | 3.791 | 0 | 0 | 0 | 0 | 0
189 | 1 | 1.048 | 0.1641 | 0.1627 | 1.051 | 0.1641 | 1.048 | 1.265 | 0.5534 | 0.4726 | 1.258 | 0.5534 | 1.265 | 4.749 | -1.275 | -0.6905 | 5.013 | -1.275 | 4.749
190 | 1 | 2.343 | 0.1641 | 0.1627 | 2.346 | 0.1641 | 2.343 | 1.356 | 0.5534 | 0.4726 | 1.349 | 0.5534 | 1.356 | 4.22 | -1.036 | -0.5843 | 4.411 | -1.036 | 4.22
191 | 1 | 1.1166 | 0.21533 | 0.21533 | 1.1166 | 0.21533 | 1.1166 | 0.4029 | 0.0086996 | 0.0086996 | 0.4029 | 0.0086996 | 0.4029 | 33.2394 | -8.5519 | -8.5519 | 33.2394 | -8.5519 | 33.2394
192 | 1 | 0.6047 | 0.1641 | 0.1627 | 0.6076 | 0.1641 | 0.6047 | 1.222 | 0.5534 | 0.4726 | 1.216 | 0.5534 | 1.222 | 5.02 | -1.405 | -0.7445 | 5.327 | -1.405 | 5.02
193 | 1 | 0.4406 | 0.1641 | 0.1627 | 0.4435 | 0.1641 | 0.4406 | 1.222 | 0.5534 | 0.4726 | 1.216 | 0.5534 | 1.222 | 5.02 | -1.405 | -0.7445 | 5.327 | -1.405 | 5.02
194 | 1 | 0.3327 | 0.1641 | 0.1627 | 0.3356 | 0.1641 | 0.3327 | 1.157 | 0.5534 | 0.4726 | 1.15 | 0.5534 | 1.157 | 5.465 | -1.627 | -0.8319 | 5.851 | -1.627 | 5.465
195 | 1 | 2.343 | 0.1641 | 0.1627 | 2.346 | 0.1641 | 2.343 | 1.356 | 0.5534 | 0.4726 | 1.349 | 0.5534 | 1.356 | 4.22 | -1.036 | -0.5843 | 4.411 | -1.036 | 4.22
196 | 1 | 0.3327 | 0.1641 | 0.1627 | 0.3356 | 0.1641 | 0.3327 | 1.157 | 0.5534 | 0.4726 | 1.15 | 0.5534 | 1.157 | 5.465 | -1.627 | -0.8319 | 5.851 | -1.627 | 5.465
197 | 1 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0 | 0 | 0 | 0 | 0 | 1.379 | 0 | 0 | 0 | 0 | 0 | 4.217
198 | 1 | 1.1166 | 0.21533 | 0.21533 | 1.1166 | 0.21533 | 1.1166 | 0.4029 | 0.0086996 | 0.0086996 | 0.4029 | 0.0086996 | 0.4029 | 33.2394 | -8.5519 | -8.5519 | 33.2394 | -8.5519 | 33.2394
199 | 1 | 1.048 | 0.1641 | 0.1627 | 1.051 | 0.1641 | 1.048 | 1.265 | 0.5534 | 0.4726 | 1.258 | 0.5534 | 1.265 | 4.749 | -1.275 | -0.6905 | 5.013 | -1.275 | 4.749
200 | 1 | 1.1166 | 0.21533 | 0.21533 | 1.1166 | 0.21533 | 1.1166 | 0.4029 | 0.0086996 | 0.0086996 | 0.4029 | 0.0086996 | 0.4029 | 33.2394 | -8.5519 | -8.5519 | 33.2394 | -8.5519 | 33.2394
201 | 1 | 2.342 | 0 | 0 | 0 | 0 | 0 | 1.358 | 0 | 0 | 0 | 0 | 0 | 3.791 | 0 | 0 | 0 | 0 | 0
202 | 1 | 1.573 | 0.1641 | 0.1627 | 1.576 | 0.1641 | 1.573 | 1.293 | 0.5534 | 0.4726 | 1.286 | 0.5534 | 1.293 | 4.586 | -1.2 | -0.6579 | 4.826 | -1.2 | 4.586
203 | 1 | 1.048 | 0.1641 | 0.1627 | 1.051 | 0.1641 | 1.048 | 1.265 | 0.5534 | 0.4726 | 1.258 | 0.5534 | 1.265 | 4.749 | -1.275 | -0.6905 | 5.013 | -1.275 | 4.749
204 | 1 | 1.573 | 0.1641 | 0.1627 | 1.576 | 0.1641 | 1.573 | 1.293 | 0.5534 | 0.4726 | 1.286 | 0.5534 | 1.293 | 4.586 | -1.2 | -0.6579 | 4.826 | -1.2 | 4.586
205 | 1 | 0.4406 | 0.1641 | 0.1627 | 0.4435 | 0.1641 | 0.4406 | 1.222 | 0.5534 | 0.4726 | 1.216 | 0.5534 | 1.222 | 5.02 | -1.405 | -0.7445 | 5.327 | -1.405 | 5.02
206 | 1 | 1.048 | 0.1641 | 0.1627 | 1.051 | 0.1641 | 1.048 | 1.265 | 0.5534 | 0.4726 | 1.258 | 0.5534 | 1.265 | 4.749 | -1.275 | -0.6905 | 5.013 | -1.275 | 4.749
207 | 1 | 1.573 | 0.1641 | 0.1627 | 1.576 | 0.1641 | 1.573 | 1.293 | 0.5534 | 0.4726 | 1.286 | 0.5534 | 1.293 | 4.586 | -1.2 | -0.6579 | 4.826 | -1.2 | 4.586
208 | 1 | 0 | 0 | 0 | 1.048 | 0.1627 | 1.048 | 0 | 0 | 0 | 1.265 | 0.4726 | 1.265 | 0 | 0 | 0 | 4.425 | -1.015 | 4.425
209 | 1 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0 | 0 | 0 | 0 | 0 | 1.379 | 0 | 0 | 0 | 0 | 0 | 4.217
210 | 1 | 1.1166 | 0.21533 | 0.21533 | 1.1166 | 0.21533 | 1.1166 | 0.4029 | 0.0086996 | 0.0086996 | 0.4029 | 0.0086996 | 0.4029 | 33.2394 | -8.5519 | -8.5519 | 33.2394 | -8.5519 | 33.2394
211 | 1 | 0.4406 | 0.1641 | 0.1627 | 0.4435 | 0.1641 | 0.4406 | 1.222 | 0.5534 | 0.4726 | 1.216 | 0.5534 | 1.222 | 5.02 | -1.405 | -0.7445 | 5.327 | -1.405 | 5.02
212 | 1 | 1.048 | 0.1641 | 0.1627 | 1.051 | 0.1641 | 1.048 | 1.265 | 0.5534 | 0.4726 | 1.258 | 0.5534 | 1.265 | 4.749 | -1.275 | -0.6905 | 5.013 | -1.275 | 4.749
213 | 1 | 0.3327 | 0.1641 | 0.1627 | 0.3356 | 0.1641 | 0.3327 | 1.157 | 0.5534 | 0.4726 | 1.15 | 0.5534 | 1.157 | 5.465 | -1.627 | -0.8319 | 5.851 | -1.627 | 5.465
214 | 1 | 0.6047 | 0.1641 | 0.1627 | 0.6076 | 0.1641 | 0.6047 | 1.222 | 0.5534 | 0.4726 | 1.216 | 0.5534 | 1.222 | 5.02 | -1.405 | -0.7445 | 5.327 | -1.405 | 5.02
215 | 1 | 0.4406 | 0.1641 | 0.1627 | 0.4435 | 0.1641 | 0.4406 | 1.222 | 0.5534 | 0.4726 | 1.216 | 0.5534 | 1.222 | 5.02 | -1.405 | -0.7445 | 5.327 | -1.405 | 5.02
216 | 1 | 0.4406 | 0.1641 | 0.1627 | 0.4435 | 0.1641 | 0.4406 | 1.222 | 0.5534 | 0.4726 | 1.216 | 0.5534 | 1.222 | 5.02 | -1.405 | -0.7445 | 5.327 | -1.405 | 5.02
217 | 1 | 1.048 | 0.1641 | 0.1627 | 1.051 | 0.1641 | 1.048 | 1.265 | 0.5534 | 0.4726 | 1.258 | 0.5534 | 1.265 | 4.749 | -1.275 | -0.6905 | 5.013 | -1.275 | 4.749
218 | 1 | 2.343 | 0.1641 | 0.1627 | 2.346 | 0.1641 | 2.343 | 1.356 | 0.5534 | 0.4726 | 1.349 | 0.5534 | 1.356 | 4.22 | -1.036 | -0.5843 | 4.411 | -1.036 | 4.22
219 | 1 | 1.1166 | 0.21533 | 0.21533 | 1.1166 | 0.21533 | 1.1166 | 0.4029 | 0.0086996 | 0.0086996 | 0.4029 | 0.0086996 | 0.4029 | 33.2394 | -8.5519 | -8.5519 | 33.2394 | -8.5519 | 33.2394
220 | 1 | 1.051 | 0.1641 | 0.1627 | 1.054 | 0.1641 | 1.051 | 1.377 | 0.5534 | 0.4726 | 1.37 | 0.5534 | 1.377 | 4.807 | -1.302 | -0.7021 | 5.08 | -1.302 | 4.807
221 | 1 | 1.051 | 0.1641 | 0.1627 | 1.054 | 0.1641 | 1.051 | 1.377 | 0.5534 | 0.4726 | 1.37 | 0.5534 | 1.377 | 4.807 | -1.302 | -0.7021 | 5.08 | -1.302 | 4.807
222 | 1 | 2.343 | 0.1641 | 0.1627 | 2.346 | 0.1641 | 2.343 | 1.356 | 0.5534 | 0.4726 | 1.349 | 0.5534 | 1.356 | 4.22 | -1.036 | -0.5843 | 4.411 | -1.036 | 4.22
223 | 1 | 1.048 | 0.1641 | 0.1627 | 1.051 | 0.1641 | 1.048 | 1.265 | 0.5534 | 0.4726 | 1.258 | 0.5534 | 1.265 | 4.749 | -1.275 | -0.6905 | 5.013 | -1.275 | 4.749
224 | 1 | 0 | 0 | 0 | 1.048 | 0.1627 | 1.048 | 0 | 0 | 0 | 1.265 | 0.4726 | 1.265 | 0 | 0 | 0 | 4.425 | -1.015 | 4.425
225 | 1 | 0.3327 | 0.1641 | 0.1627 | 0.3356 | 0.1641 | 0.3327 | 1.157 | 0.5534 | 0.4726 | 1.15 | 0.5534 | 1.157 | 5.465 | -1.627 | -0.8319 | 5.851 | -1.627 | 5.465
226 | 1 | 0.40063 | 0.21533 | 0.21533 | 0.40063 | 0.21533 | 0.40063 | 0.32307 | 0.0086669 | 0.0086669 | 0.32307 | 0.0086669 | 0.32307 | 52.5085 | -7.5843 | -7.5843 | 52.5085 | -7.5843 | 52.5085
227 | 1 | 1.051 | 0.1641 | 0.1627 | 1.054 | 0.1641 | 1.051 | 1.377 | 0.5534 | 0.4726 | 1.37 | 0.5534 | 1.377 | 4.807 | -1.302 | -0.7021 | 5.08 | -1.302 | 4.807
228 | 1 | 0 | 0 | 0 | 0 | 0 | 1.047 | 0 | 0 | 0 | 0 | 0 | 1.267 | 0 | 0 | 0 | 0 | 0 | 4.176
229 | 1 | 0.4406 | 0.1641 | 0.1627 | 0.4435 | 0.1641 | 0.4406 | 1.222 | 0.5534 | 0.4726 | 1.216 | 0.5534 | 1.222 | 5.02 | -1.405 | -0.7445 | 5.327 | -1.405 | 5.02
230 | 1 | 1.572 | 0 | 0 | 0 | 0 | 0 | 1.294 | 0 | 0 | 0 | 0 | 0 | 4.06 | 0 | 0 | 0 | 0 | 0
231 | 1 | 1.572 | 0 | 0 | 0 | 0 | 0 | 1.294 | 0 | 0 | 0 | 0 | 0 | 4.06 | 0 | 0 | 0 | 0 | 0
232 | 1 | 1.048 | 0.1641 | 0.1627 | 1.051 | 0.1641 | 1.048 | 1.265 | 0.5534 | 0.4726 | 1.258 | 0.5534 | 1.265 | 4.749 | -1.275 | -0.6905 | 5.013 | -1.275 | 4.749
233 | 1 | 1.1166 | 0.21533 | 0.21533 | 1.1166 | 0.21533 | 1.1166 | 0.4029 | 0.0086996 | 0.0086996 | 0.4029 | 0.0086996 | 0.4029 | 33.2394 | -8.5519 | -8.5519 | 33.2394 | -8.5519 | 33.2394
234 | 1 | 0.6047 | 0.1641 | 0.1627 | 0.6076 | 0.1641 | 0.6047 | 1.222 | 0.5534 | 0.4726 | 1.216 | 0.5534 | 1.222 | 5.02 | -1.405 | -0.7445 | 5.327 | -1.405 | 5.02
235 | 1 | 1.573 | 0.1641 | 0.1627 | 1.576 | 0.1641 | 1.573 | 1.293 | 0.5534 | 0.4726 | 1.286 | 0.5534 | 1.293 | 4.586 | -1.2 | -0.6579 | 4.826 | -1.2 | 4.586
236 | 1 | 0.3327 | 0.1641 | 0.1627 | 0.3356 | 0.1641 | 0.3327 | 1.157 | 0.5534 | 0.4726 | 1.15 | 0.5534 | 1.157 | 5.465 | -1.627 | -0.8319 | 5.851 | -1.627 | 5.465
237 | 1 | 2.342 | 0 | 0 | 0 | 0 | 0 | 1.358 | 0 | 0 | 0 | 0 | 0 | 3.791 | 0 | 0 | 0 | 0 | 0
238 | 1 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0 | 0 | 0 | 0 | 0 | 1.379 | 0 | 0 | 0 | 0 | 0 | 4.217
239 | 1 | 1.048 | 0.1641 | 0.1627 | 1.051 | 0.1641 | 1.048 | 1.265 | 0.5534 | 0.4726 | 1.258 | 0.5534 | 1.265 | 4.749 | -1.275 | -0.6905 | 5.013 | -1.275 | 4.749
240 | 1 | 1.1166 | 0.21533 | 0.21533 | 1.1166 | 0.21533 | 1.1166 | 0.4029 | 0.0086996 | 0.0086996 | 0.4029 | 0.0086996 | 0.4029 | 33.2394 | -8.5519 | -8.5519 | 33.2394 | -8.5519 | 33.2394
241 | 1 | 0.3327 | 0.1641 | 0.1627 | 0.3356 | 0.1641 | 0.3327 | 1.157 | 0.5534 | 0.4726 | 1.15 | 0.5534 | 1.157 | 5.465 | -1.627 | -0.8319 | 5.851 | -1.627 | 5.465
242 | 1 | 1.573 | 0.1641 | 0.1627 | 1.576 | 0.1641 | 1.573 | 1.293 | 0.5534 | 0.4726 | 1.286 | 0.5534 | 1.293 | 4.586 | -1.2 | -0.6579 | 4.826 | -1.2 | 4.586
243 | 1 | 1.047 | 0 | 0 | 0 | 0 | 0 | 1.267 | 0 | 0 | 0 | 0 | 0 | 4.176 | 0 | 0 | 0 | 0 | 0
244 | 1 | 0.3327 | 0.1641 | 0.1627 | 0.3356 | 0.1641 | 0.3327 | 1.157 | 0.5534 | 0.4726 | 1.15 | 0.5534 | 1.157 | 5.465 | -1.627 | -0.8319 | 5.851 | -1.627 | 5.465
245 | 1 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0 | 0 | 0 | 0 | 0 | 1.379 | 0 | 0 | 0 | 0 | 0 | 4.217
246 | 1 | 2.343 | 0 | 0.1627 | 0 | 0 | 2.343 | 1.356 | 0 | 0.4726 | 0 | 0 | 1.356 | 3.976 | 0 | -0.8276 | 0 | 0 | 3.976
247 | 1 | 0.4406 | 0.1641 | 0.1627 | 0.4435 | 0.1641 | 0.4406 | 1.222 | 0.5534 | 0.4726 | 1.216 | 0.5534 | 1.222 | 5.02 | -1.405 | -0.7445 | 5.327 | -1.405 | 5.02
248 | 1 | 2.342 | 0 | 0 | 0 | 0 | 0 | 1.358 | 0 | 0 | 0 | 0 | 0 | 3.791 | 0 | 0 | 0 | 0 | 0
249 | 1 | 1.1166 | 0.21533 | 0.21533 | 1.1166 | 0.21533 | 1.1166 | 0.4029 | 0.0086996 | 0.0086996 | 0.4029 | 0.0086996 | 0.4029 | 33.2394 | -8.5519 | -8.5519 | 33.2394 | -8.5519 | 33.2394
250 | 1 | 0.4406 | 0.1641 | 0.1627 | 0.4435 | 0.1641 | 0.4406 | 1.222 | 0.5534 | 0.4726 | 1.216 | 0.5534 | 1.222 | 5.02 | -1.405 | -0.7445 | 5.327 | -1.405 | 5.02
251 | 1 | 2.343 | 0.1641 | 0.1627 | 2.346 | 0.1641 | 2.343 | 1.356 | 0.5534 | 0.4726 | 1.349 | 0.5534 | 1.356 | 4.22 | -1.036 | -0.5843 | 4.411 | -1.036 | 4.22
252 | 1 | 0 | 0 | 0 | 2.342 | 0 | 0 | 0 | 0 | 0 | 1.358 | 0 | 0 | 0 | 0 | 0 | 3.791 | 0 | 0
253 | 1 | 0.4406 | 0.1641 | 0.1627 | 0.4435 | 0.1641 | 0.4406 | 1.222 | 0.5534 | 0.4726 | 1.216 | 0.5534 | 1.222 | 5.02 | -1.405 | -0.7445 | 5.327 | -1.405 | 5.02
254 | 1 | 1.048 | 0.1641 | 0.1627 | 1.051 | 0.1641 | 1.048 | 1.265 | 0.5534 | 0.4726 | 1.258 | 0.5534 | 1.265 | 4.749 | -1.275 | -0.6905 | 5.013 | -1.275 | 4.749
255 | 1 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0 | 0 | 0 | 0 | 0 | 1.379 | 0 | 0 | 0 | 0 | 0 | 4.217
256 | 1 | 0.67363 | 0.21533 | 0.21533 | 0.67363 | 0.21533 | 0.67363 | 0.36027 | 0.0086669 | 0.0086669 | 0.36027 | 0.0086669 | 0.36027 | 44.1993 | -6.3841 | -6.3841 | 44.1993 | -6.3841 | 44.1993
257 | 1 | 1.047 | 0 | 0 | 0 | 0 | 0 | 1.267 | 0 | 0 | 0 | 0 | 0 | 4.176 | 0 | 0 | 0 | 0 | 0
258 | 1 | 0.3327 | 0.1641 | 0.1627 | 0.3356 | 0.1641 | 0.3327 | 1.157 | 0.5534 | 0.4726 | 1.15 | 0.5534 | 1.157 | 5.465 | -1.627 | -0.8319 | 5.851 | -1.627 | 5.465
259 | 1 | 1.051 | 0.1641 | 0.1627 | 1.054 | 0.1641 | 1.051 | 1.377 | 0.5534 | 0.4726 | 1.37 | 0.5534 | 1.377 | 4.807 | -1.302 | -0.7021 | 5.08 | -1.302 | 4.807
260 | 1 | 1.051 | 0.1641 | 0.1627 | 1.054 | 0.1641 | 1.051 | 1.377 | 0.5534 | 0.4726 | 1.37 | 0.5534 | 1.377 | 4.807 | -1.302 | -0.7021 | 5.08 | -1.302 | 4.807
261 | 1 | 2.343 | 0.1641 | 0.1627 | 2.346 | 0.1641 | 2.343 | 1.356 | 0.5534 | 0.4726 | 1.349 | 0.5534 | 1.356 | 4.22 | -1.036 | -0.5843 | 4.411 | -1.036 | 4.22
262 | 1 | 0 | 0 | 0 | 0 | 0 | 1.572 | 0 | 0 | 0 | 0 | 0 | 1.294 | 0 | 0 | 0 | 0 | 0 | 4.06
263 | 1 | 2.343 | 0.1641 | 0.1627 | 2.346 | 0.1641 | 2.343 | 1.356 | 0.5534 | 0.4726 | 1.349 | 0.5534 | 1.356 | 4.22 | -1.036 | -0.5843 | 4.411 | -1.036 | 4.22
264 | 1 | 2.342 | 0 | 0 | 0 | 0 | 0 | 1.358 | 0 | 0 | 0 | 0 | 0 | 3.791 | 0 | 0 | 0 | 0 | 0
265 | 1 | 1.1166 | 0.21533 | 0.21533 | 1.1166 | 0.21533 | 1.1166 | 0.4029 | 0.0086996 | 0.0086996 | 0.4029 | 0.0086996 | 0.4029 | 33.2394 | -8.5519 | -8.5519 | 33.2394 | -8.5519 | 33.2394
266 | 1 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0 | 0 | 0 | 0 | 0 | 1.379 | 0 | 0 | 0 | 0 | 0 | 4.217
267 | 1 | 1.048 | 0.1641 | 0.1627 | 1.051 | 0.1641 | 1.048 | 1.265 | 0.5534 | 0.4726 | 1.258 | 0.5534 | 1.265 | 4.749 | -1.275 | -0.6905 | 5.013 | -1.275 | 4.749
268 | 1 | 0.4406 | 0.1641 | 0.1627 | 0.4435 | 0.1641 | 0.4406 | 1.222 | 0.5534 | 0.4726 | 1.216 | 0.5534 | 1.222 | 5.02 | -1.405 | -0.7445 | 5.327 | -1.405 | 5.02
269 | 1 | 1.1166 | 0.21533 | 0.21533 | 1.1166 | 0.21533 | 1.1166 | 0.4029 | 0.0086996 | 0.0086996 | 0.4029 | 0.0086996 | 0.4029 | 33.2394 | -8.5519 | -8.5519 | 33.2394 | -8.5519 | 33.2394
270 | 1 | 0.6047 | 0.1641 | 0.1627 | 0.6076 | 0.1641 | 0.6047 | 1.222 | 0.5534 | 0.4726 | 1.216 | 0.5534 | 1.222 | 5.02 | -1.405 | -0.7445 | 5.327 | -1.405 | 5.02
271 | 1 | 0 | 0 | 0 | 2.342 | 0 | 0 | 0 | 0 | 0 | 1.358 | 0 | 0 | 0 | 0 | 0 | 3.791 | 0 | 0
272 | 1 | 1.048 | 0.1641 | 0.1627 | 1.051 | 0.1641 | 1.048 | 1.265 | 0.5534 | 0.4726 | 1.258 | 0.5534 | 1.265 | 4.749 | -1.275 | -0.6905 | 5.013 | -1.275 | 4.749
273 | 1 | 1.573 | 0.1641 | 0.1627 | 1.576 | 0.1641 | 1.573 | 1.293 | 0.5534 | 0.4726 | 1.286 | 0.5534 | 1.293 | 4.586 | -1.2 | -0.6579 | 4.826 | -1.2 | 4.586
274 | 1 | 1.572 | 0 | 0 | 0 | 0 | 0 | 1.294 | 0 | 0 | 0 | 0 | 0 | 4.06 | 0 | 0 | 0 | 0 | 0
275 | 1 | 0.3327 | 0.1641 | 0.1627 | 0.3356 | 0.1641 | 0.3327 | 1.157 | 0.5534 | 0.4726 | 1.15 | 0.5534 | 1.157 | 5.465 | -1.627 | -0.8319 | 5.851 | -1.627 | 5.465
276 | 1 | 0.3327 | 0.1641 | 0.1627 | 0.3356 | 0.1641 | 0.3327 | 1.157 | 0.5534 | 0.4726 | 1.15 | 0.5534 | 1.157 | 5.465 | -1.627 | -0.8319 | 5.851 | -1.627 | 5.465
277 | 1 | 0.3327 | 0.1641 | 0.1627 | 0.3356 | 0.1641 | 0.3327 | 1.157 | 0.5534 | 0.4726 | 1.15 | 0.5534 | 1.157 | 5.465 | -1.627 | -0.8319 | 5.851 | -1.627 | 5.465
278 | 1 | 0.6047 | 0.1641 | 0.1627 | 0.6076 | 0.1641 | 0.6047 | 1.222 | 0.5534 | 0.4726 | 1.216 | 0.5534 | 1.222 | 5.02 | -1.405 | -0.7445 | 5.327 | -1.405 | 5.02
279 | 1 | 2.342 | 0 | 0 | 0 | 0 | 0 | 1.358 | 0 | 0 | 0 | 0 | 0 | 3.791 | 0 | 0 | 0 | 0 | 0
280 | 1 | 0.6047 | 0.1641 | 0.1627 | 0.6076 | 0.1641 | 0.6047 | 1.222 | 0.5534 | 0.4726 | 1.216 | 0.5534 | 1.222 | 5.02 | -1.405 | -0.7445 | 5.327 | -1.405 | 5.02
281 | 1 | 0.3327 | 0.1641 | 0.1627 | 0.3356 | 0.1641 | 0.3327 | 1.157 | 0.5534 | 0.4726 | 1.15 | 0.5534 | 1.157 | 5.465 | -1.627 | -0.8319 | 5.851 | -1.627 | 5.465
282 | 1 | 2.342 | 0 | 0 | 0 | 0 | 0 | 1.358 | 0 | 0 | 0 | 0 | 0 | 3.791 | 0 | 0 | 0 | 0 | 0
283 | 1 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0 | 0 | 0 | 0 | 0 | 1.379 | 0 | 0 | 0 | 0 | 0 | 4.217
284 | 1 | 0.4406 | 0.1641 | 0.1627 | 0.4435 | 0.1641 | 0.4406 | 1.222 | 0.5534 | 0.4726 | 1.216 | 0.5534 | 1.222 | 5.02 | -1.405 | -0.7445 | 5.327 | -1.405 | 5.02
285 | 1 | 1.048 | 0.1641 | 0.1627 | 1.051 | 0.1641 | 1.048 | 1.265 | 0.5534 | 0.4726 | 1.258 | 0.5534 | 1.265 | 4.749 | -1.275 | -0.6905 | 5.013 | -1.275 | 4.749
286 | 1 | 2.342 | 0 | 0 | 0 | 0 | 0 | 1.358 | 0 | 0 | 0 | 0 | 0 | 3.791 | 0 | 0 | 0 | 0 | 0
287 | 1 | 1.048 | 0.1641 | 0.1627 | 1.051 | 0.1641 | 1.048 | 1.265 | 0.5534 | 0.4726 | 1.258 | 0.5534 | 1.265 | 4.749 | -1.275 | -0.6905 | 5.013 | -1.275 | 4.749
288 | 1 | 2.343 | 0 | 0.1627 | 0 | 0 | 2.343 | 1.356 | 0 | 0.4726 | 0 | 0 | 1.356 | 3.976 | 0 | -0.8276 | 0 | 0 | 3.976
289 | 1 | 1.048 | 0.1641 | 0.1627 | 1.051 | 0.1641 | 1.048 | 1.265 | 0.5534 | 0.4726 | 1.258 | 0.5534 | 1.265 | 4.749 | -1.275 | -0.6905 | 5.013 | -1.275 | 4.749
290 | 1 | 1.1166 | 0.21533 | 0.21533 | 1.1166 | 0.21533 | 1.1166 | 0.4029 | 0.0086996 | 0.0086996 | 0.4029 | 0.0086996 | 0.4029 | 33.2394 | -8.5519 | -8.5519 | 33.2394 | -8.5519 | 33.2394
291 | 1 | 1.048 | 0.1641 | 0.1627 | 1.051 | 0.1641 | 1.048 | 1.265 | 0.5534 | 0.4726 | 1.258 | 0.5534 | 1.265 | 4.749 | -1.275 | -0.6905 | 5.013 | -1.275 | 4.749
292 | 1 | 1.048 | 0.1641 | 0.1627 | 1.051 | 0.1641 | 1.048 | 1.265 | 0.5534 | 0.4726 | 1.258 | 0.5534 | 1.265 | 4.749 | -1.275 | -0.6905 | 5.013 | -1.275 | 4.749
293 | 1 | 1.048 | 0.1641 | 0.1627 | 1.051 | 0.1641 | 1.048 | 1.265 | 0.5534 | 0.4726 | 1.258 | 0.5534 | 1.265 | 4.749 | -1.275 | -0.6905 | 5.013 | -1.275 | 4.749
294 | 1 | 0.4406 | 0.1641 | 0.1627 | 0.4435 | 0.1641 | 0.4406 | 1.222 | 0.5534 | 0.4726 | 1.216 | 0.5534 | 1.222 | 5.02 | -1.405 | -0.7445 | 5.327 | -1.405 | 5.02
295 | 1 | 0 | 0 | 0 | 0 | 0 | 1.1166 | 0 | 0 | 0 | 0 | 0 | 0.4029 | 0 | 0 | 0 | 0 | 0 | 33.2394
296 | 1 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0 | 0 | 0 | 0 | 0 | 1.379 | 0 | 0 | 0 | 0 | 0 | 4.217
297 | 1 | 0.3327 | 0.1641 | 0.1627 | 0.3356 | 0.1641 | 0.3327 | 1.157 | 0.5534 | 0.4726 | 1.15 | 0.5534 | 1.157 | 5.465 | -1.627 | -0.8319 | 5.851 | -1.627 | 5.465
298 | 1 | 0.4406 | 0.1641 | 0.1627 | 0.4435 | 0.1641 | 0.4406 | 1.222 | 0.5534 | 0.4726 | 1.216 | 0.5534 | 1.222 | 5.02 | -1.405 | -0.7445 | 5.327 | -1.405 | 5.02

## Loads
Node | Y=1, D=0 | Alfa (PQ=0, I=1, Z=2) | Ph-1 (kW) | Ph-1 (kVAr) | Ph-2 (kW) | Ph-2 (kWAr) | Ph-3 (KW) | Ph-3 (kVAr)
230 | 1 | 0 | 2.56 | 0 | 2.56 | 0 | 2.56 | 0
269 | 1 | 0 | 0 | 0 | 0 | 0 | 63.5 | 30
291 | 1 | 0 | 0 | 0 | 107.736 | 52 | 0 | 0
50 | 1 | 0 | 11.604 | 5 | 0 | 0 | 0 | 0
53 | 1 | 0 | 0 | 0 | 13.456 | 5 | 36.348 | 16
298 | 1 | 0 | 10.32 | 4 | 0 | 0 | 0 | 0
19 | 1 | 0 | 0 | 0 | 19.62 | 9 | 0 | 0
161 | 1 | 0 | 0 | 0 | 30.456 | 14 | 0 | 0
192 | 1 | 0 | 39.232 | 19 | 0 | 0 | 0 | 0
158 | 1 | 0 | 7.32 | 3 | 0 | 0 | 0 | 0
244 | 1 | 0 | 19.808 | 9 | 0 | 0 | 0 | 0
225 | 1 | 0 | 10.212 | 3 | 10.212 | 3 | 3.84 | 1
164 | 1 | 0 | 11.616 | 3 | 11.616 | 3 | 4.408 | 1
278 | 1 | 0 | 12.424 | 2 | 3.048 | 0 | 3.048 | 0
58 | 1 | 0 | 0 | 0 | 0.404 | 0 | 1.072 | 0
66 | 1 | 0 | 0.556 | 0 | 1.468 | 0 | 0 | 0
183 | 1 | 0 | 26.228 | 12 | 0 | 0 | 0 | 0
199 | 1 | 0 | 0 | 0 | 0 | 0 | 16.76 | 8
6 | 1 | 0 | 26.048 | 18 | 26.048 | 18 | 9.888 | 7
147 | 1 | 0 | 23.02 | 5 | 8.736 | 2 | 23.02 | 5
11 | 1 | 0 | 0 | 0 | 0 | 0 | 10.24 | 4
236 | 1 | 0 | 21.44 | 10 | 0 | 0 | 0 | 0
292 | 1 | 0 | 0 | 0 | 7.232 | 3 | 0 | 0
163 | 1 | 0 | 80.516 | 39 | 0 | 0 | 0 | 0
174 | 1 | 0 | 33.692 | 16 | 0 | 0 | 0 | 0
133 | 1 | 0 | 6.412 | 1 | 22.208 | 6 | 22.208 | 6
152 | 1 | 0 | 1.464 | 0 | 0 | 0 | 0 | 0
253 | 1 | 0 | 10.128 | 5 | 26.68 | 13 | 26.68 | 13
218 | 1 | 0 | 0 | 0 | 44.332 | 21 | 0 | 0
231 | 1 | 0 | 0 | 0 | 0 | 0 | 47.604 | 23
61 | 1 | 0 | 0 | 0 | 3.384 | 2 | 8.948 | 6
193 | 1 | 0 | 0 | 0 | 60.444 | 29 | 0 | 0
207 | 1 | 0 | 6.444 | 4 | 6.444 | 4 | 2.404 | 1
277 | 1 | 0 | 32.972 | 15 | 0 | 0 | 0 | 0
57 | 1 | 0 | 10.56 | 1 | 10.56 | 1 | 4.008 | 0
17 | 1 | 0 | 0 | 0 | 22.604 | 10 | 0 | 0
29 | 1 | 0 | 0 | 0 | 0 | 0 | 12.54 | 6
22 | 1 | 0 | 10.916 | 5 | 0 | 0 | 1.732 | 0
166 | 1 | 0 | 0 | 0 | 0 | 0 | 16.996 | 8
279 | 1 | 0 | 22.396 | 3 | 22.396 | 3 | 22.396 | 3
224 | 1 | 0 | 2.932 | 1 | 2.932 | 1 | 2.932 | 1
14 | 1 | 0 | 2.436 | 0 | 2.436 | 0 | 0.924 | 0
123 | 1 | 0 | 0 | 0 | 7.2267 | 5 | 7.2267 | 5
30 | 1 | 0 | 0 | 0 | 12.864 | 6 | 0 | 0
280 | 1 | 0 | 0 | 0 | 22.808 | 11 | 0 | 0
71 | 1 | 0 | 0 | 0 | 0 | 0 | 17.616 | 8
167 | 1 | 0 | 0 | 0 | 19.296 | 9 | 0 | 0
245 | 1 | 0 | 0 | 0 | 0 | 0 | 26.548 | 12
246 | 1 | 0 | 51.136 | 24 | 0 | 0 | 0 | 0
82 | 1 | 0 | 2 | 1 | 2 | 1 | 2 | 1
2 | 1 | 0 | 8.008 | 2 | 8.008 | 2 | 8.008 | 2
266 | 1 | 0 | 15.176 | 2 | 15.176 | 2 | 5.72 | 0
191 | 1 | 0 | 0 | 0 | 4.188 | 2 | 0 | 0
281 | 1 | 0 | 11.52 | 3 | 11.52 | 3 | 11.52 | 3
222 | 1 | 0 | 27.944 | 4 | 27.944 | 4 | 27.944 | 4
299 | 1 | 0 | 0 | 0 | 0 | 0 | 57.232 | 27
142 | 1 | 0 | 0 | 0 | 0 | 0 | 39.868 | 19
52 | 1 | 0 | 0 | 0 | 0 | 0 | 34.656 | 16
295 | 1 | 0 | 37.948 | 18 | 0 | 0 | 0 | 0
77 | 1 | 0 | 9.404 | 2 | 24.78 | 7 | 24.78 | 7
284 | 1 | 0 | 0 | 0 | 0.876 | 0 | 2.312 | 0
28 | 1 | 0 | 0 | 0 | 0 | 0 | 12.292 | 5
188 | 1 | 0 | 19.256 | 9 | 0 | 0 | 0 | 0
78 | 1 | 0 | 0.74667 | 0 | 0.74667 | 0 | 0.74667 | 0
223 | 1 | 0 | 0 | 0 | 0 | 0 | 42.192 | 20
39 | 1 | 0 | 17.6 | 8 | 0 | 0 | 0 | 0
283 | 1 | 0 | 32.996 | 14 | 32.996 | 14 | 32.996 | 14
81 | 1 | 0 | 0 | 0 | 0 | 0 | 32.98 | 15
238 | 1 | 0 | 43.344 | 21 | 0 | 0 | 0 | 0
153 | 1 | 0 | 9.2 | 4 | 9.2 | 4 | 9.2 | 4
160 | 1 | 0 | 0.9 | 0 | 0 | 0 | 0 | 0
184 | 1 | 0 | 0 | 0 | 0 | 0 | 20.42 | 9
293 | 1 | 0 | 10.452 | 4 | 10.452 | 4 | 10.452 | 4
141 | 1 | 0 | 4.32 | 2 | 0 | 0 | 0 | 0
5 | 1 | 0 | 0 | 0 | 0 | 0 | 10.212 | 4
262 | 1 | 0 | 4.36 | 0 | 4.36 | 0 | 4.36 | 0
237 | 1 | 0 | 0 | 0 | 8.56 | 4 | 0 | 0
121 | 1 | 0 | 0 | 0 | 43.704 | 21 | 0 | 0
228 | 1 | 0 | 45.936 | 22 | 7.32 | 3 | 7.32 | 3
101 | 1 | 0 | 0 | 0 | 0 | 0 | 63.344 | 30
255 | 1 | 0 | 0 | 0 | 0 | 0 | 59.82 | 28
104 | 1 | 0 | 9.944 | 3 | 0 | 0 | 3.76 | 1
210 | 1 | 0 | 27.556 | 13 | 0 | 0 | 0 | 0
263 | 1 | 0 | 26.292 | 9 | 26.292 | 9 | 6.44 | 1
221 | 1 | 0 | 22.576 | 10 | 22.576 | 10 | 0.42 | 0
33 | 1 | 0 | 1.324 | 0 | 1.324 | 0 | 1.324 | 0
242 | 1 | 0 | 1.068 | 0 | 1.068 | 0 | 1.068 | 0
235 | 1 | 0 | 17.704 | 1 | 17.704 | 1 | 17.704 | 1
240 | 1 | 0 | 0 | 0 | 0 | 0 | 18.944 | 9
226 | 1 | 0 | 20.084 | 3 | 20.084 | 3 | 20.084 | 3
270 | 1 | 0 | 7.056 | 3 | 0.156 | 0 | 0 | 0
72 | 1 | 0 | 14.688 | 7 | 0 | 0 | 0 | 0
258 | 1 | 0 | 0 | 0 | 0 | 0 | 50.752 | 24
75 | 1 | 0 | 0.928 | 0 | 0 | 0 | 0 | 0
243 | 1 | 0 | 0 | 0 | 0 | 0 | 16.256 | 7
286 | 1 | 0 | 3.84 | 1 | 0 | 0 | 0 | 0
256 | 1 | 0 | 9.332 | 2 | 9.332 | 2 | 9.332 | 2
48 | 1 | 0 | 16.212 | 3 | 16.212 | 3 | 16.212 | 3
135 | 1 | 0 | 22.012 | 10 | 0 | 0 | 0 | 0
143 | 1 | 0 | 0.64 | 0 | 1.688 | 1 | 1.688 | 1
190 | 1 | 0 | 0 | 0 | 0 | 0 | 8.088 | 3
220 | 1 | 0 | 0 | 0 | 0 | 0 | 2.048 | 0
124 | 1 | 0 | 0 | 0 | 5.192 | 2 | 0 | 0
95 | 1 | 0 | 0.64 | 0 | 1.688 | 1 | 1.688 | 1
211 | 1 | 0 | 0 | 0 | 10.86 | 5 | 0 | 0
213 | 1 | 0 | 19.744 | 9 | 0 | 0 | 0 | 0
289 | 1 | 0 | 13.12 | 4 | 13.12 | 4 | 13.12 | 4
296 | 1 | 0 | 0 | 0 | 0 | 0 | 26.912 | 13
185 | 1 | 0 | 4.716 | 1 | 4.716 | 1 | 1.792 | 0
45 | 1 | 0 | 1.92 | 2 | 1.92 | 2 | 1.92 | 2
249 | 1 | 0 | 0 | 0 | 2.96 | 0 | 7.96 | 1
271 | 1 | 0 | 15.572 | 3 | 15.572 | 3 | 15.572 | 3
54 | 1 | 0 | 11.652 | 5 | 0 | 0 | 0 | 0
180 | 1 | 0 | 0 | 0 | 0 | 0 | 57.236 | 27
251 | 1 | 0 | 36.36 | 17 | 0 | 0 | 0 | 0
265 | 1 | 0 | 83.86 | 14 | 83.86 | 14 | 83.86 | 14
227 | 1 | 0 | 2.432 | 1 | 9.216 | 4 | 9.216 | 4
282 | 1 | 0 | 9.064 | 3 | 9.064 | 3 | 9.064 | 3
259 | 1 | 0 | 0 | 0 | 3.908 | 1 | 0 | 0
51 | 1 | 0 | 22.808 | 11 | 0 | 0 | 0 | 0
294 | 1 | 0 | 16.852 | 7 | 16.852 | 7 | 16.852 | 7
268 | 1 | 0 | 0 | 0 | 0 | 0 | 33.892 | 16
115 | 1 | 0 | 0 | 0 | 0.076 | 0 | 0 | 0
288 | 1 | 0 | 103.456 | 33 | 103.456 | 33 | 103.456 | 33
155 | 1 | 0 | 4.864 | 2 | 0 | 0 | 0 | 0
287 | 1 | 0 | 62.856 | 30 | 0 | 0 | 0 | 0
70 | 1 | 0 | 0 | 0 | 33.96 | 16 | 0 | 0
168 | 1 | 0 | 3.632 | 0 | 3.632 | 0 | 17.744 | 4
241 | 1 | 0 | 0.852 | 0 | 0 | 0 | 0 | 0
165 | 1 | 0 | 0 | 0 | 10.044 | 4 | 0 | 0
254 | 1 | 0 | 0 | 0 | 0.616 | 0 | 0 | 0
234 | 1 | 0 | 1.6 | 0 | 1.6 | 0 | 1.6 | 0
195 | 1 | 0 | 0 | 0 | 34.356 | 16 | 0 | 0
47 | 1 | 0 | 0 | 0 | 0 | 0 | 0.408 | 0
10 | 1 | 0 | 0 | 0 | 5.316 | 2 | 14.056 | 5
208 | 1 | 0 | 12.16 | 5 | 0 | 0 | 0 | 0
202 | 1 | 0 | 0 | 0 | 0 | 0 | 31.764 | 15
179 | 1 | 0 | 0 | 0 | 7.38 | 0 | 28.308 | 7
267 | 1 | 0 | 76.364 | 0 | 76.364 | 0 | 76.364 | 0
248 | 1 | 0 | 3.732 | 1 | 3.732 | 1 | 3.732 | 1
276 | 1 | 0 | 21.384 | 3 | 21.384 | 3 | 21.384 | 3
297 | 1 | 0 | 12.888 | 2 | 12.888 | 2 | 12.888 | 2
216 | 1 | 0 | 0.72 | 0 | 0.72 | 0 | 0.72 | 0
219 | 1 | 0 | 0 | 0 | 0 | 0 | 67.472 | 32
9 | 1 | 0 | 0 | 0 | 21.872 | 9 | 2.452 | 0
114 | 1 | 0 | 13.568 | 0 | 5.132 | 0 | 0 | 0
84 | 1 | 0 | 6.48 | 3 | 0 | 0 | 0 | 0
131 | 1 | 0 | 0 | 0 | 0 | 0 | 11.04 | 5

## Graphic
Node | Pos X | Pos Y | NodeID
1 | 2241347 | 230933 | 12KV_X7441
2 | 2238594 | 229101 | 12KV_Y1380
3 | 2242518 | 232662 | 12KV_PB0753
4 | 2239554 | 229663 | 12KV_Y1005
5 | 2240587 | 229821 | 12KV_Y1122
6 | 2242119 | 234025 | 12KV_X4579
7 | 2241043 | 229816 | 12KV_Y1255
8 | 2238611 | 231444 | 12KV_X7266
9 | 2237131 | 228243 | 12KV_Y1037
10 | 2240252 | 230668 | 12KV_X7069
11 | 2240354 | 229923 | 12KV_Y1121
12 | 2238622 | 229402 | 12KV_Y1250
13 | 2241569 | 230068 | 12KV_X7470
14 | 2242260 | 234514 | 12KV_X4417
15 | 2239381 | 229137 | 12KV_Y1007
16 | 2237297 | 228318 | 12KV_Y1305
17 | 2239227 | 230915 | 12KV_X7240
18 | 2238822 | 230784 | 12KV_Y1346
19 | 2239497 | 230799 | 12KV_X7005
20 | 2240652 | 230977 | 12KV_X7070
21 | 2238670 | 229001 | 12KV_Y1281
22 | 2243446 | 233254 | 12KV_X4351
23 | 2237299 | 228373 | 12KV_Y1304
24 | 2236860 | 231511 | 12KV_PB1880
25 | 2240313 | 230170 | 12KV_Y1229
26 | 2241236 | 231431 | 12KV_X7109
27 | 2242732 | 232587 | 12KV_X7487
28 | 2241093 | 229934 | 12KV_X7189
29 | 2241138 | 230040 | 12KV_X7190
30 | 2242317 | 232556 | 12KV_X7P012
31 | 2240270 | 230598 | 12KV_X7242
32 | 2238712 | 230832 | 12KV_Y1325
33 | 2237480 | 227618 | 12KV_Y1539
34 | 2239684 | 230719 | 12KV_X7004
35 | 2238214 | 229815 | 12KV_Y1420
36 | 2238101 | 229614 | 12KV_Y1409
37 | 2239201 | 229854 | 12KV_Y1253
38 | 2239291 | 230583 | 12KV_Y1348
39 | 2239052 | 228410 | 12KV_Y1031
40 | 2237867 | 229724 | 12KV_Y1408
41 | 2238322 | 229509 | 12KV_Y1258
42 | 2238145 | 229033 | 12KV_Y1227
43 | 2241409 | 230629 | 12KV_X7P024
44 | 2239661 | 229599 | 12KV_Y1210
45 | 2242631 | 234355 | 12KV_X4601
46 | 2238950 | 231034 | 12KV_X7222
47 | 2237485 | 228516 | 12KV_Y1314
48 | 2243165 | 233311 | 12KV_X1P9128
49 | 2239827 | 230147 | 12KV_Y1002
50 | 2238730 | 230867 | 12KV_Y1219
51 | 2239618 | 228552 | 12KV_Y1224
52 | 2240805 | 229721 | 12KV_Y1123
53 | 2237071 | 228122 | 12KV_Y1324
54 | 2240553 | 230476 | 12KV_X7087
55 | 2242445 | 234436 | 12KV_X4600
56 | 2239862 | 230630 | 12KV_X7003
57 | 2242511 | 233856 | 12KV_X4565
58 | 2238251 | 229036 | 12KV_Y1335
59 | 2237800 | 227534 | 12KV_Y1536
60 | 2243409 | 233119 | 12KV_X7119
61 | 2240015 | 230483 | 12KV_X7068
62 | 2236935 | 228092 | 12KV_Y1036
63 | 2237312 | 232477 | 12KV_PB1881
64 | 2237562 | 228888 | 12KV_PB1840
65 | 2240884 | 230680 | 12KV_X7093
66 | 2238941 | 232437 | 12KV_X7419
67 | 2243265 | 234127 | 12KV_X4082
68 | 2238371 | 230913 | 12KV_Y1608
69 | 2239407 | 230840 | 12KV_X7269
70 | 2240819 | 231106 | 12KV_X7107
71 | 2239293 | 228944 | 12KV_Y1016
72 | 2240694 | 229147 | 12KV_Y1236
73 | 2238608 | 230876 | 12KV_Y1345
74 | 2239967 | 230467 | 12KV_X7057
75 | 2239254 | 228857 | 12KV_Y1008
76 | 2239884 | 230123 | 12KV_Y1207
77 | 2238139 | 227705 | 12KV_Y1535
78 | 2238429 | 229814 | 12KV_Y1431
79 | 2237539 | 229577 | 12KV_Y1317
80 | 2241020 | 230274 | 12KV_X7210
81 | 2240648 | 229500 | 12KV_Y1186
82 | 2238544 | 231292 | 12KV_X7139
83 | 2237163 | 231970 | 12KV_S3P009
84 | 2240407 | 230787 | 12KV_X7106
85 | 2243126 | 234150 | 12KV_X4337
86 | 2236331 | 230503 | 12KV_S3445
87 | 2240695 | 230810 | 12KV_X7091
88 | 2238013 | 227700 | 12KV_Y1533
89 | 2237806 | 228632 | 12KV_Y1313
90 | 2238369 | 229205 | 12KV_Y1228
91 | 2237392 | 229065 | 12KV_Y1321
92 | 2241605 | 232088 | 12KV_X7461
93 | 2240971 | 230678 | 12KV_X7449
94 | 2238496 | 229227 | 12KV_Y1204
95 | 2242252 | 233968 | 12KV_X4393
96 | 2241024 | 229627 | 12KV_Y1415
97 | 2237160 | 228190 | 12KV_Y1567
98 | 2239057 | 230683 | 12KV_Y1347
99 | 2241692 | 231790 | 12KV_X7111
100 | 2238315 | 229898 | 12KV_Y1421
101 | 2241513 | 230126 | 12KV_X7457
102 | 2240441 | 230483 | 12KV_X7086
103 | 2242556 | 232451 | 12KV_X7115
104 | 2238193 | 229569 | 12KV_Y1407
105 | 2237909 | 228485 | 12KV_Y1352
106 | 2237588 | 229745 | 12KV_Y1615
107 | 2240416 | 230399 | 12KV_X7225
108 | 2238691 | 229455 | 12KV_Y1387
109 | 2239672 | 230218 | 12KV_Y1217
110 | 2236545 | 230430 | 12KV_PB1785
111 | 2238502 | 231201 | 12KV_X7389
112 | 2241109 | 229619 | 12KV_Y1521
113 | 2237475 | 228378 | 12KV_Y1590
114 | 2238404 | 230985 | 12KV_Y1602
115 | 2239460 | 229314 | 12KV_Y1006
116 | 2237463 | 229313 | 12KV_Y1318
117 | 2240662 | 230430 | 12KV_X7088
118 | 2236585 | 227775 | 12KV_Y1589
119 | 2241301 | 231156 | 12KV_X7279
120 | 2237758 | 228734 | 12KV_Y1362
121 | 2239041 | 230995 | 12KV_X7241
122 | 2236537 | 230356 | 12KV_S3354
123 | 2236982 | 227856 | 12KV_Y1525
124 | 2239904 | 230328 | 12KV_Y1001
125 | 2237593 | 229764 | 12KV_Y1497
126 | 2238822 | 231087 | 12KV_X7218
127 | 2243437 | 233385 | 12KV_X4281
128 | 2240694 | 230934 | 12KV_X7394
129 | 2238929 | 231349 | 12KV_X7490
130 | 2241383 | 230757 | 12KV_X7468
131 | 2240228 | 229979 | 12KV_Y1120
132 | 2239104 | 228525 | 12KV_Y1015
133 | 2243389 | 233847 | 12KV_X4365
134 | 2236970 | 228044 | 12KV_Y1528
135 | 2240458 | 229249 | 12KV_Y1176
136 | 2237802 | 227555 | 12KV_Y1537
137 | 2238822 | 229476 | 12KV_Y1262
138 | 2237406 | 228378 | 12KV_Y1591
139 | 2241100 | 229599 | 12KV_Y1240
140 | 2239788 | 228942 | 12KV_Y1021
141 | 2242888 | 234252 | 12KV_X4338
142 | 2240379 | 230317 | 12KV_X7129
143 | 2237539 | 228300 | 12KV_Y1541
144 | 2239271 | 229185 | 12KV_Y1614
145 | 2236506 | 230371 | 12KV_S3441
146 | 2236757 | 227878 | 12KV_Y1400
147 | 2238506 | 229643 | 12KV_Y1423
148 | 2240011 | 230580 | 12KV_X7002
149 | 2240999 | 229712 | 12KV_Y1205
150 | 2243272 | 234087 | 12KV_X4336
151 | 2237850 | 227910 | 12KV_Y1542
152 | 2237128 | 231945 | 12KV_S3P007
153 | 2242901 | 232717 | 12KV_X7511
154 | 2236312 | 230462 | 12KV_S3120
155 | 2240039 | 229436 | 12KV_Y1022
156 | 2237498 | 229438 | 12KV_Y1524
157 | 2241100 | 231247 | 12KV_X7080
158 | 2240856 | 230345 | 12KV_X7090
159 | 2239673 | 228677 | 12KV_Y1223
160 | 2238499 | 229306 | 12KV_Y1385
161 | 2239171 | 228674 | 12KV_Y1014
162 | 2241801 | 231876 | 12KV_X7112
163 | 2241419 | 230644 | 12KV_X7442
164 | 2237651 | 228167 | 12KV_Y1530
165 | 2241934 | 232688 | 12KV_X7P013
166 | 2239653 | 229002 | 12KV_Y1020
167 | 2241022 | 231263 | 12KV_X7108
168 | 2241891 | 234123 | 12KV_X4001
169 | 2243556 | 233778 | 12KV_X4132
170 | 2237387 | 228440 | 12KV_Y1403
171 | 2236902 | 227959 | 12KV_Y1526
172 | 2236849 | 231114 | 12KV_S3P006
173 | 2238907 | 232116 | 12KV_X7264
174 | 2239695 | 229844 | 12KV_Y1004
175 | 2238768 | 229516 | 12KV_Y1251
176 | 2236864 | 227960 | 12KV_Y1527
177 | 2242040 | 232053 | 12KV_X7113
178 | 2237639 | 229831 | 12KV_MH0259
179 | 2240087 | 230455 | 12KV_X7215
180 | 2241449 | 230437 | 12KV_X7454
181 | 2240583 | 229195 | 12KV_Y1235
182 | 2242723 | 233763 | 12KV_X4630
183 | 2240756 | 230390 | 12KV_X7089
184 | 2240736 | 230166 | 12KV_X7130
185 | 2242528 | 234106 | 12KV_X4363
186 | 2243117 | 232884 | 12KV_X7118
187 | 2243400 | 233101 | 12KV_X7489
188 | 2239885 | 229503 | 12KV_Y1013
189 | 2243413 | 234038 | 12KV_X4080
190 | 2240702 | 230089 | 12KV_X7194
191 | 2236702 | 227897 | 12KV_Y1588
192 | 2239726 | 228800 | 12KV_Y1222
193 | 2239178 | 229884 | 12KV_Y1P001
194 | 2238296 | 229149 | 12KV_Y1611
195 | 2239531 | 229475 | 12KV_Y1118
196 | 2239198 | 229219 | 12KV_Y1168
197 | 2239865 | 230367 | 12KV_Y1216
198 | 2237976 | 227619 | 12KV_Y1534
199 | 2240693 | 229602 | 12KV_Y1185
200 | 2236666 | 230842 | 12KV_PB1786
201 | 2238390 | 229145 | 12KV_Y1351
202 | 2240924 | 229671 | 12KV_Y1242
203 | 2237641 | 227582 | 12KV_Y1538
204 | 2237660 | 228651 | 12KV_Y1039
205 | 2238243 | 228980 | 12KV_Y1616
206 | 2238114 | 229733 | 12KV_Y1419
207 | 2242322 | 232271 | 12KV_X7498
208 | 2240781 | 230727 | 12KV_X7092
209 | 2243537 | 233574 | 12KV_X4133
210 | 2240334 | 229309 | 12KV_Y1175
211 | 2238986 | 229686 | 12KV_Y1252
212 | 2238761 | 231780 | 12KV_X7265
213 | 2240183 | 229374 | 12KV_Y1115
214 | 2242378 | 233912 | 12KV_X4364
215 | 2239549 | 229047 | 12KV_Y1019
216 | 2239087 | 230347 | 12KV_Y1349
217 | 2242186 | 232811 | 12KV_PB0754
218 | 2238887 | 231246 | 12KV_X7212
219 | 2241691 | 230110 | 12KV_X7P004
220 | 2240294 | 229632 | 12KV_Y1140
221 | 2239509 | 230092 | 12KV_Y1248
222 | 2239440 | 229669 | 12KV_Y1P014
223 | 2241054 | 229771 | 12KV_Y1520
224 | 2238545 | 231548 | 12KV_X7P020
225 | 2242078 | 234593 | 12KV_X4418
226 | 2238724 | 229208 | 12KV_Y1P012
227 | 2237228 | 228463 | 12KV_Y1416
228 | 2240255 | 230214 | 12KV_Y1315
229 | 2241437 | 231590 | 12KV_X7110
230 | 2242547 | 232627 | 12KV_X7488
231 | 2241155 | 230014 | 12KV_X7456
232 | 2239397 | 230006 | 12KV_Y1218
233 | 2238911 | 228206 | 12KV_Y1017
234 | 2238010 | 229196 | 12KV_Y1P009
235 | 2241502 | 230580 | 12KV_X7P002
236 | 2240443 | 230989 | 12KV_X7049
237 | 2243151 | 233303 | 12KV_X7306
238 | 2239564 | 228419 | 12KV_Y1619
239 | 2240723 | 229671 | 12KV_Y1184
240 | 2240344 | 229751 | 12KV_Y1139
241 | 2237435 | 232775 | 12KV_S3P008
242 | 2238264 | 230581 | 12KV_Y1P022
243 | 2239769 | 230012 | 12KV_Y1003
244 | 2240915 | 229052 | 12KV_Y1237
245 | 2240032 | 230061 | 12KV_Y1119
246 | 2241110 | 230236 | 12KV_X7452
247 | 2238051 | 228617 | 12KV_Y1040
248 | 2238185 | 229276 | 12KV_Y1P004
249 | 2237391 | 228968 | 12KV_Y1388
250 | 2241555 | 232081 | 12KV_X7P003
251 | 2240905 | 230495 | 12KV_X7430
252 | 2241659 | 232094 | 12KV_X7460
253 | 2238349 | 229902 | 12KV_Y1549
254 | 2237903 | 228844 | 12KV_Y1095
255 | 2241512 | 229827 | 12KV_X7458
256 | 2237789 | 228353 | 12KV_Y1P021
257 | 2238461 | 231108 | 12KV_X7267
258 | 2241212 | 229624 | 12KV_Y1522
259 | 2237244 | 229365 | 12KV_Y1284
260 | 2241257 | 231320 | 12KV_X7278
261 | 2236629 | 230311 | 12KV_MH0258
262 | 2238878 | 231372 | 12KV_X7491
263 | 2239857 | 230607 | 12KV_X7001
264 | 2243365 | 233854 | 12KV_X4662
265 | 2237763 | 227649 | 12KV_Y1P008
266 | 2238961 | 229402 | 12KV_Y1296
267 | 2238914 | 229295 | 12KV_Y1P015
268 | 2240666 | 230006 | 12KV_Y1124
269 | 2241110 | 229449 | 12KV_Y1239
270 | 2242759 | 234308 | 12KV_X4339
271 | 2239352 | 229286 | 12KV_Y1P018
272 | 2236352 | 230443 | 12KV_S3446
273 | 2240050 | 230669 | 12KV_X7053
274 | 2236424 | 227529 | 12KV_Y4246
275 | 2243409 | 234029 | 12KV_X4335
276 | 2237916 | 227970 | 12KV_Y1543
277 | 2239956 | 229205 | 12KV_Y1P013
278 | 2241154 | 231231 | 12KV_X7167
279 | 2237753 | 228036 | 12KV_Y1531
280 | 2241930 | 232705 | 12KV_X7P014
281 | 2241330 | 231165 | 12KV_X7447
282 | 2238825 | 232060 | 12KV_X7486
283 | 2241540 | 230615 | 12KV_X7P018
284 | 2238651 | 229348 | 12KV_Y1203
285 | 2240145 | 230450 | 12KV_X7517
286 | 2240554 | 229038 | 12KV_Y1275
287 | 2241085 | 230323 | 12KV_X7450
288 | 2242693 | 233630 | 12KV_X4P026
289 | 2242995 | 232992 | 12KV_X7P017
290 | 2243545 | 234005 | 12KV_X4581
291 | 2239287 | 229951 | 12KV_Y1P002
292 | 2239095 | 229287 | 12KV_Y1232
293 | 2236837 | 227611 | 12KV_Y1P005
294 | 2238251 | 228920 | 12KV_Y1P019
295 | 2241049 | 230793 | 12KV_X7448
296 | 2240831 | 229458 | 12KV_Y1316
297 | 2238883 | 230108 | 12KV_Y1350
298 | 2241929 | 233062 | 12KV_X7P022
299 | 2241655 | 230313 | 12KV_X7P005

## Regulators
Line | Tap A | Tap B | Tap C

## Switches
NODE1 | NODE2 | Closed=1